## Sheet1
Description | Mhr
- - -
cable tray ladder type (galvanized steel) 150 6" WIDTH & SMALLER (150 mm.) | 0.729
cable tray ladder type (galvanized steel) 300 12" WIDTH (300 mm.) | 0.892
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 0.973
cable tray ladder type (galvanized steel) 450 18" WIDTH (450 mm.) | 1.014
cable tray ladder type (galvanized steel) 600 24" WIDTH (600 mm.) | 1.216
cable tray ladder type (galvanized steel) 750 30" WIDTH (750 mm.) | 1.419
cable tray ladder type (galvanized steel) 900 36" WIDTH (900 mm.) | 1.824
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 1.925
cable tray ladder type (galvanized steel) - - | -
cable tray ladder type (aluminum) 150 6" WIDTH & SMALLER (150 mm.) | 0.584
cable tray ladder type (aluminum) 300 12" WIDTH (300 mm.) | 0.713
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 0.778
cable tray ladder type (aluminum) 450 18" WIDTH (450 mm.) | 0.811
cable tray ladder type (aluminum) 600 24" WIDTH (600 mm.) | 0.973
cable tray ladder type (aluminum) 750 30" WIDTH (750 mm.) | 1.135
cable tray ladder type (aluminum) 900 36" WIDTH (900 mm.) | 1.46
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 1.541
cable tray ladder type (aluminum) - - | -
cable tray solid bottom (galvanized steel) 150 6" WIDTH & SMALLER (150 mm.) | 0.993
cable tray solid bottom (galvanized steel) 300 12" WIDTH (300 mm.) | 1.177
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 1.223
cable tray solid bottom (galvanized steel) 450 18" WIDTH (450 mm.) | 1.246
cable tray solid bottom (galvanized steel) 600 24" WIDTH (600 mm.) | 1.679
cable tray solid bottom (galvanized steel) 750 30" WIDTH (750 mm.) | 2.013
cable tray solid bottom (galvanized steel) 900 36" WIDTH (900 mm.) | 2.095
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 2.211
cable tray solid bottom (galvanized steel) - - | -
cable tray (ea) cable tray bends 150 6" WIDTH & SMALLER (150 mm.) | 0.876
cable tray (ea) cable tray bends 300 12" WIDTH (300 mm.) | 1.082
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 1.15
cable tray (ea) cable tray bends 450 18" WIDTH (450 mm.) | 1.185
cable tray (ea) cable tray bends 600 24" WIDTH (600 mm.) | 1.339
cable tray (ea) cable tray bends 750 30" WIDTH (750 mm.) | 1.494
cable tray (ea) cable tray bends 900 36" WIDTH (900 mm.) | 1.751
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 1.848
cable tray (ea) cable tray bends - - | -
cable tray (ea) cable tray tee 150 6" WIDTH & SMALLER (150 mm.) | 0.927
cable tray (ea) cable tray tee 300 12" WIDTH (300 mm.) | 1.133
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 1.202
cable tray (ea) cable tray tee 450 18" WIDTH (450 mm.) | 1.236
cable tray (ea) cable tray tee 600 24" WIDTH (600 mm.) | 1.391
cable tray (ea) cable tray tee 750 30" WIDTH (750 mm.) | 1.545
cable tray (ea) cable tray tee 900 36" WIDTH (900 mm.) | 1.803
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 1.903
cable tray (ea) cable tray tee - - | -
cable tray cable tray cover 150 6" WIDTH & SMALLER (150 mm.) | 0.129
cable tray cable tray cover 300 12" WIDTH (300 mm.) | 0.169
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 0.207
cable tray cable tray cover 450 18" WIDTH (450 mm.) | 0.227
cable tray cable tray cover 600 24" WIDTH (600 mm.) | 0.307
cable tray cable tray cover 750 30" WIDTH (750 mm.) | 0.375
cable tray cable tray cover 900 36" WIDTH (900 mm.) | 0.422
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 0.446
cable tray cable tray cover - - | -
cable tray cable tray barriers 150 6" WIDTH & SMALLER (150 mm.) | 0.541
cable tray cable tray barriers 300 12" WIDTH (300 mm.) | 0.507
cable tray cable tray barriers 450 16" WIDTH (400 mm.) | 0.461
cable tray cable tray barriers 450 18" WIDTH (450 mm.) | 0.439
cable tray cable tray barriers 600 24" WIDTH (600 mm.) | 0.406
cable tray cable tray barriers 750 30" WIDTH (750 mm.) | 0.372
cable tray cable tray barriers 900 36" WIDTH (900 mm.) | 0.372
cable tray cable tray cover 900 37" WIDTH (950 mm.) | 0.372
conduit RSC/IMC above ground 1/2" 1/2" DIAMETER ( 15 mm.) | 0.381
conduit RSC/IMC above ground 3/4" 3/4" DIAMETER ( 20 mm.) | 0.422
conduit RSC/IMC above ground 1" 1" DIAMETER ( 25 mm.) | 0.515
conduit RSC/IMC above ground 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.567
conduit RSC/IMC above ground 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.618
conduit RSC/IMC above ground 2" 2" DIAMETER ( 50 mm.) | 0.752
conduit RSC/IMC above ground 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.958
conduit RSC/IMC above ground 3" 3" DIAMETER ( 75 mm.) | 1.205
conduit RSC/IMC above ground 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.411
conduit RSC/IMC above ground 4" 4" DIAMETER (100 mm.) | 1.617
conduit RSC/IMC above ground 5" 5" DIAMETER (125 mm.) | 1.854
conduit RSC/IMC above ground 6" 6" DIAMETER (150 mm.) | 2.091
conduit RSC/IMC above ground - - | -
conduit RSC/IMC under ground 1/2" 1/2" DIAMETER ( 15 mm.) | 0.361
conduit RSC/IMC under ground 3/4" 3/4" DIAMETER ( 20 mm.) | 0.402
conduit RSC/IMC under ground 1" 1" DIAMETER ( 25 mm.) | 0.433
conduit RSC/IMC under ground 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.536
conduit RSC/IMC under ground 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.567
conduit RSC/IMC under ground 2" 2" DIAMETER ( 50 mm.) | 0.67
conduit RSC/IMC under ground 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.742
conduit RSC/IMC under ground 3" 3" DIAMETER ( 75 mm.) | 0.855
conduit RSC/IMC under ground 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.896
conduit RSC/IMC under ground 4" 4" DIAMETER (100 mm.) | 0.948
conduit RSC/IMC under ground 5" 5" DIAMETER (125 mm.) | 1.03
conduit RSC/IMC under ground 6" 6" DIAMETER (150 mm.) | 1.391
conduit RSC/IMC under ground - - | -
conduit RSC/IMC embedded 1/2" 1/2" DIAMETER ( 15 mm.) | 0.412
conduit RSC/IMC embedded 3/4" 3/4" DIAMETER ( 20 mm.) | 0.464
conduit RSC/IMC embedded 1" 1" DIAMETER ( 25 mm.) | 0.546
conduit RSC/IMC embedded 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.597
conduit RSC/IMC embedded 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.67
conduit RSC/IMC embedded 2" 2" DIAMETER ( 50 mm.) | 0.834
conduit RSC/IMC embedded 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 1.133
conduit RSC/IMC embedded 3" 3" DIAMETER ( 75 mm.) | 1.442
conduit RSC/IMC embedded 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.545
conduit RSC/IMC embedded 4" 4" DIAMETER (100 mm.) | 2.06
conduit RSC/IMC embedded 5" 5" DIAMETER (125 mm.) | 2.215
conduit RSC/IMC embedded 6" 6" DIAMETER (150 mm.) | 2.575
conduit RSC/IMC embedded - - | -
conduit EMT 1/2" 1/2" DIAMETER ( 15 mm.) | 0.309
conduit EMT 3/4" 3/4" DIAMETER ( 20 mm.) | 0.35
conduit EMT 1" 1" DIAMETER ( 25 mm.) | 0.412
conduit EMT 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.464
conduit EMT 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.505
conduit EMT 2" 2" DIAMETER ( 50 mm.) | 0.567
conduit EMT 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.618
conduit EMT 3" 3" DIAMETER ( 75 mm.) | 0.67
conduit EMT 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.803
conduit EMT 4" 4" DIAMETER (100 mm.) | 1.236
conduit EMT 5" 5" DIAMETER (125 mm.) | N.A.
conduit EMT 6" 6" DIAMETER (150 mm.) | N.A.
conduit FMC (ordinary) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.206
conduit FMC (ordinary) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.237
conduit FMC (ordinary) 1" 1" DIAMETER ( 25 mm.) | 0.309
conduit FMC (ordinary) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.35
conduit FMC (ordinary) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.412
conduit FMC (ordinary) 2" 2" DIAMETER ( 50 mm.) | 0.464
conduit FMC (ordinary) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.515
conduit FMC (ordinary) 3" 3" DIAMETER ( 75 mm.) | 0.824
conduit FMC (ordinary) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.03
conduit FMC (ordinary) 4" 4" DIAMETER (100 mm.) | 1.288
conduit FMC (ordinary) 5" 5" DIAMETER (125 mm.) | 1.442
conduit FMC (ordinary) 6" 6" DIAMETER (150 mm.) | 1.648
conduit FMC (ordinary) - - | -
conduit FMC (liquid tight) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.237
conduit FMC (liquid tight) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.268
conduit FMC (liquid tight) 1" 1" DIAMETER ( 25 mm.) | 0.361
conduit FMC (liquid tight) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.402
conduit FMC (liquid tight) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.474
conduit FMC (liquid tight) 2" 2" DIAMETER ( 50 mm.) | 0.536
conduit FMC (liquid tight) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.597
conduit FMC (liquid tight) 3" 3" DIAMETER ( 75 mm.) | 0.948
conduit FMC (liquid tight) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.185
conduit FMC (liquid tight) 4" 4" DIAMETER (100 mm.) | 1.483
conduit FMC (liquid tight) 5" 5" DIAMETER (125 mm.) | 1.658
conduit FMC (liquid tight) 6" 6" DIAMETER (150 mm.) | 1.895
conduit FMC (liquid tight) - - | -
conduit NMC 1/2" 1/2" DIAMETER ( 15 mm.) | 0.233
conduit NMC 3/4" 3/4" DIAMETER ( 20 mm.) | 0.273
conduit NMC 1" 1" DIAMETER ( 25 mm.) | 0.402
conduit NMC 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.425
conduit NMC 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.433
conduit NMC 2" 2" DIAMETER ( 50 mm.) | 0.561
conduit NMC 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.71
conduit NMC 3" 3" DIAMETER ( 75 mm.) | 0.793
conduit NMC 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.922
conduit NMC 4" 4" DIAMETER (100 mm.) | 1.138
conduit NMC 5" 5" DIAMETER (125 mm.) | 1.339
conduit NMC 6" 6" DIAMETER (150 mm.) | 1.545
conduit NMC - - | -
conduit fitting service entrance cap 1/2" 1/2" DIAMETER ( 15 mm.) | 0.309
conduit fitting service entrance cap 3/4" 3/4" DIAMETER ( 20 mm.) | 0.361
conduit fitting service entrance cap 1" 1" DIAMETER ( 25 mm.) | 0.412
conduit fitting service entrance cap 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.464
conduit fitting service entrance cap 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.515
conduit fitting service entrance cap 2" 2" DIAMETER ( 50 mm.) | 0.567
conduit fitting service entrance cap 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.721
conduit fitting service entrance cap 3" 3" DIAMETER ( 75 mm.) | 0.876
conduit fitting service entrance cap 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.03
conduit fitting service entrance cap 4" 4" DIAMETER (100 mm.) | 1.133
conduit fitting service entrance cap 5" 5" DIAMETER (125 mm.) | 1.442
conduit fitting service entrance cap 6" 6" DIAMETER (150 mm.) | 1.648
conduit fitting conduit unions 1/2" 1/2" DIAMETER ( 15 mm.) | 0.206
conduit fitting conduit unions 3/4" 3/4" DIAMETER ( 20 mm.) | 0.258
conduit fitting conduit unions 1" 1" DIAMETER ( 25 mm.) | 0.309
conduit fitting conduit unions 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.361
conduit fitting conduit unions 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.361
conduit fitting conduit unions 2" 2" DIAMETER ( 50 mm.) | 0.412
conduit fitting conduit unions 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.464
conduit fitting conduit unions 3" 3" DIAMETER ( 75 mm.) | 0.515
conduit fitting conduit unions 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.567
conduit fitting conduit unions 4" 4" DIAMETER (100 mm.) | 0.618
conduit fitting conduit unions 5" 5" DIAMETER (125 mm.) | 0.824
conduit fitting conduit unions 6" 6" DIAMETER (150 mm.) | 1.03
conduit fitting conduit elbows 1/2" 1/2" DIAMETER ( 15 mm.) | 0.155
conduit fitting conduit elbows 3/4" 3/4" DIAMETER ( 20 mm.) | 0.155
conduit fitting conduit elbows 1" 1" DIAMETER ( 25 mm.) | 0.206
conduit fitting conduit elbows 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.206
conduit fitting conduit elbows 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.258
conduit fitting conduit elbows 2" 2" DIAMETER ( 50 mm.) | 0.258
conduit fitting conduit elbows 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.361
conduit fitting conduit elbows 3" 3" DIAMETER ( 75 mm.) | 0.464
conduit fitting conduit elbows 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.515
conduit fitting conduit elbows 4" 4" DIAMETER (100 mm.) | 0.567
conduit fitting conduit elbows 5" 5" DIAMETER (125 mm.) | 0.773
conduit fitting conduit elbows 6" 6" DIAMETER (150 mm.) | 0.927
conduit fitting conduit elbows - - | -
conduit fitting condulets 1/2" 1/2" DIAMETER ( 15 mm.) | 0.206
conduit fitting condulets 3/4" 3/4" DIAMETER ( 20 mm.) | 0.258
conduit fitting condulets 1" 1" DIAMETER ( 25 mm.) | 0.309
conduit fitting condulets 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.361
conduit fitting condulets 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.361
conduit fitting condulets 2" 2" DIAMETER ( 50 mm.) | 0.412
conduit fitting condulets 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.464
conduit fitting condulets 3" 3" DIAMETER ( 75 mm.) | 0.515
conduit fitting condulets 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.567
conduit fitting condulets 4" 4" DIAMETER (100 mm.) | 0.618
conduit fitting condulets 5" 5" DIAMETER (125 mm.) | 0.773
conduit fitting condulets 6" 6" DIAMETER (150 mm.) | 0.927
conduit fitting condulets - - | -
conduit fitting expansion joints 1/2" 1/2" DIAMETER ( 15 mm.) | 0.412
conduit fitting expansion joints 3/4" 3/4" DIAMETER ( 20 mm.) | 0.464
conduit fitting expansion joints 1" 1" DIAMETER ( 25 mm.) | 0.515
conduit fitting expansion joints 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.567
conduit fitting expansion joints 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.618
conduit fitting expansion joints 2" 2" DIAMETER ( 50 mm.) | 0.67
conduit fitting expansion joints 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.824
conduit fitting expansion joints 3" 3" DIAMETER ( 75 mm.) | 1.03
conduit fitting expansion joints 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.185
conduit fitting expansion joints 4" 4" DIAMETER (100 mm.) | 1.339
conduit fitting expansion joints 5" 5" DIAMETER (125 mm.) | 1.545
conduit fitting expansion joints 6" 6" DIAMETER (150 mm.) | 2.06
conduit fitting lock nut and metallic bushing 1/2" 1/2" DIAMETER ( 15 mm.) | 0.155
conduit fitting lock nut and metallic bushing 3/4" 3/4" DIAMETER ( 20 mm.) | 0.155
conduit fitting lock nut and metallic bushing 1" 1" DIAMETER ( 25 mm.) | 0.206
conduit fitting lock nut and metallic bushing 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.206
conduit fitting lock nut and metallic bushing 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.258
conduit fitting lock nut and metallic bushing 2" 2" DIAMETER ( 50 mm.) | 0.258
conduit fitting lock nut and metallic bushing 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.309
conduit fitting lock nut and metallic bushing 3" 3" DIAMETER ( 75 mm.) | 0.361
conduit fitting lock nut and metallic bushing 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.412
conduit fitting lock nut and metallic bushing 4" 4" DIAMETER (100 mm.) | 0.515
conduit fitting lock nut and metallic bushing 5" 5" DIAMETER (125 mm.) | 0.618
conduit fitting lock nut and metallic bushing 6" 6" DIAMETER (150 mm.) | 0.773
conduit fitting eys sealing fitting 1/2" 1/2" DIAMETER ( 15 mm.) | 0.464
conduit fitting eys sealing fitting 3/4" 3/4" DIAMETER ( 20 mm.) | 0.464
conduit fitting eys sealing fitting 1" 1" DIAMETER ( 25 mm.) | 0.567
conduit fitting eys sealing fitting 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.567
conduit fitting eys sealing fitting 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.67
conduit fitting eys sealing fitting 2" 2" DIAMETER ( 50 mm.) | 0.876
conduit fitting eys sealing fitting 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 1.03
conduit fitting eys sealing fitting 3" 3" DIAMETER ( 75 mm.) | 1.442
conduit fitting eys sealing fitting 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 1.545
conduit fitting eys sealing fitting 4" 4" DIAMETER (100 mm.) | 1.803
conduit fitting eys sealing fitting 5" 5" DIAMETER (125 mm.) | 2.06
conduit fitting eys sealing fitting 6" 6" DIAMETER (150 mm.) | 2.318
conduit fitting eys sealing fitting - - | -
conduit fitting flexible straight connector (ordinary) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.155
conduit fitting flexible straight connector (ordinary) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.155
conduit fitting flexible straight connector (ordinary) 1" 1" DIAMETER ( 25 mm.) | 0.206
conduit fitting flexible straight connector (ordinary) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.258
conduit fitting flexible straight connector (ordinary) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.309
conduit fitting flexible straight connector (ordinary) 2" 2" DIAMETER ( 50 mm.) | 0.412
conduit fitting flexible straight connector (ordinary) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.464
conduit fitting flexible straight connector (ordinary) 3" 3" DIAMETER ( 75 mm.) | 0.515
conduit fitting flexible straight connector (ordinary) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.567
conduit fitting flexible straight connector (ordinary) 4" 4" DIAMETER (100 mm.) | 0.618
conduit fitting flexible straight connector (ordinary) 5" 5" DIAMETER (125 mm.) | 0.773
conduit fitting flexible straight connector (ordinary) 6" 6" DIAMETER (150 mm.) | 1.03
conduit fitting flexible straight connector (ordinary) - - | -
conduit fitting flexible straight connector (liquid tight) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.206
conduit fitting flexible straight connector (liquid tight) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.206
conduit fitting flexible straight connector (liquid tight) 1" 1" DIAMETER ( 25 mm.) | 0.258
conduit fitting flexible straight connector (liquid tight) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.309
conduit fitting flexible straight connector (liquid tight) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.412
conduit fitting flexible straight connector (liquid tight) 2" 2" DIAMETER ( 50 mm.) | 0.567
conduit fitting flexible straight connector (liquid tight) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.618
conduit fitting flexible straight connector (liquid tight) 3" 3" DIAMETER ( 75 mm.) | 0.67
conduit fitting flexible straight connector (liquid tight) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.773
conduit fitting flexible straight connector (liquid tight) 4" 4" DIAMETER (100 mm.) | 0.927
conduit fitting flexible straight connector (liquid tight) 5" 5" DIAMETER (125 mm.) | 1.03
conduit fitting flexible straight connector (liquid tight) 6" 6" DIAMETER (150 mm.) | 1.288
conduit fitting flexible angle connector (ordinary) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.206
conduit fitting flexible angle connector (ordinary) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.206
conduit fitting flexible angle connector (ordinary) 1" 1" DIAMETER ( 25 mm.) | 0.258
conduit fitting flexible angle connector (ordinary) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.309
conduit fitting flexible angle connector (ordinary) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.361
conduit fitting flexible angle connector (ordinary) 2" 2" DIAMETER ( 50 mm.) | 0.464
conduit fitting flexible angle connector (ordinary) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.515
conduit fitting flexible angle connector (ordinary) 3" 3" DIAMETER ( 75 mm.) | 0.567
conduit fitting flexible angle connector (ordinary) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.618
conduit fitting flexible angle connector (ordinary) 4" 4" DIAMETER (100 mm.) | 0.721
conduit fitting flexible angle connector (ordinary) 5" 5" DIAMETER (125 mm.) | 0.824
conduit fitting flexible angle connector (ordinary) 6" 6" DIAMETER (150 mm.) | 1.03
conduit fitting flexible angle connector (liquid tight) 1/2" 1/2" DIAMETER ( 15 mm.) | 0.258
conduit fitting flexible angle connector (liquid tight) 3/4" 3/4" DIAMETER ( 20 mm.) | 0.258
conduit fitting flexible angle connector (liquid tight) 1" 1" DIAMETER ( 25 mm.) | 0.309
conduit fitting flexible angle connector (liquid tight) 1-1/4" 1-1/4" DIAMETER ( 32 mm.) | 0.361
conduit fitting flexible angle connector (liquid tight) 1-1/2" 1-1/2" DIAMETER ( 38 mm.) | 0.464
conduit fitting flexible angle connector (liquid tight) 2" 2" DIAMETER ( 50 mm.) | 0.618
conduit fitting flexible angle connector (liquid tight) 2-1/2" 2-1/2" DIAMETER ( 65 mm.) | 0.773
conduit fitting flexible angle connector (liquid tight) 3" 3" DIAMETER ( 75 mm.) | 0.876
conduit fitting flexible angle connector (liquid tight) 3-1/2" 3-1/2" DIAMETER ( 90 mm.) | 0.979
conduit fitting flexible angle connector (liquid tight) 4" 4" DIAMETER (100 mm.) | 1.185
conduit fitting flexible angle connector (liquid tight) 5" 5" DIAMETER (125 mm.) | 1.339
conduit fitting flexible angle connector (liquid tight) 6" 6" DIAMETER (150 mm.) | 1.545
conduit fitting flexible angle connector (liquid tight) - - | -
cable bus duct cable bus duct 225AMP FEEDER DUCT COPPER | 1.984
cable bus duct cable bus duct 225AMP FEEDER DUCT ALUMINUM | 1.984
cable bus duct cable bus duct 225AMP PLUG - IN DUCT COPPER | 1.984
cable bus duct cable bus duct 225AMP PLUG - IN DUCT ALUMINUM | 1.984
cable bus duct cable bus duct 225AMP FEEDER DUCT COPPER | 1.707
cable bus duct cable bus duct 225AMP FEEDER DUCT ALUMINUM | 1.707
cable bus duct cable bus duct 225AMP PLUG - IN DUCT COPPER | 1.707
cable bus duct cable bus duct 225AMP PLUG - IN DUCT ALUMINUM | 1.707
cable bus duct cable bus duct 400AMP FEEDER DUCT COPPER | 2.475
cable bus duct cable bus duct 400AMP FEEDER DUCT ALUMINUM | 2.475
cable bus duct cable bus duct 400AMP PLUG - IN DUCT COPPER | 2.475
cable bus duct cable bus duct 400AMP PLUG - IN DUCT ALUMINUM | 2.475
cable bus duct cable bus duct 400AMP FEEDER DUCT COPPER | 2.198
cable bus duct cable bus duct 400AMP FEEDER DUCT ALUMINUM | 2.198
cable bus duct cable bus duct 400AMP PLUG - IN DUCT COPPER | 2.198
cable bus duct cable bus duct 400AMP PLUG - IN DUCT ALUMINUM | 2.198
cable bus duct cable bus duct 600AMP FEEDER DUCT COPPER | 2.753
cable bus duct cable bus duct 600AMP FEEDER DUCT ALUMINUM | 2.753
cable bus duct cable bus duct 600AMP PLUG - IN DUCT COPPER | 2.753
cable bus duct cable bus duct 600AMP PLUG - IN DUCT ALUMINUM | 2.753
cable bus duct cable bus duct 600AMP FEEDER DUCT COPPER | 2.475
cable bus duct cable bus duct 600AMP FEEDER DUCT ALUMINUM | 2.475
cable bus duct cable bus duct 600AMP PLUG - IN DUCT COPPER | 2.475
cable bus duct cable bus duct 600AMP PLUG - IN DUCT ALUMINUM | 2.475
cable bus duct cable bus duct 800AMP FEEDER DUCT COPPER | 3.186
cable bus duct cable bus duct 800AMP FEEDER DUCT ALUMINUM | 3.186
cable bus duct cable bus duct 800AMP PLUG - IN DUCT COPPER | 3.186
cable bus duct cable bus duct 800AMP PLUG - IN DUCT ALUMINUM | 3.186
cable bus duct cable bus duct 800AMP FEEDER DUCT COPPER | 2.753
cable bus duct cable bus duct 800AMP FEEDER DUCT ALUMINUM | 2.753
cable bus duct cable bus duct 800AMP PLUG - IN DUCT COPPER | 2.753
cable bus duct cable bus duct 800AMP PLUG - IN DUCT ALUMINUM | 2.753
cable bus duct cable bus duct 1000AMP FEEDER DUCT COPPER | 3.63
cable bus duct cable bus duct 1000AMP FEEDER DUCT ALUMINUM | 3.63
cable bus duct cable bus duct 1000AMP PLUG - IN DUCT COPPER | 3.63
cable bus duct cable bus duct 1000AMP PLUG - IN DUCT ALUMINUM | 3.63
cable bus duct cable bus duct 1000AMP FEEDER DUCT COPPER | 3.075
cable bus duct cable bus duct 1000AMP FEEDER DUCT ALUMINUM | 3.075
cable bus duct cable bus duct 1000AMP PLUG - IN DUCT COPPER | 3.075
cable bus duct cable bus duct 1000AMP PLUG - IN DUCT ALUMINUM | 3.075
cable bus duct cable bus duct 1200AMP FEEDER DUCT COPPER | 3.799
cable bus duct cable bus duct 1200AMP FEEDER DUCT ALUMINUM | 3.799
cable bus duct cable bus duct 1200AMP PLUG - IN DUCT COPPER | 3.799
cable bus duct cable bus duct 1200AMP PLUG - IN DUCT ALUMINUM | 3.799
cable bus duct cable bus duct 1200AMP FEEDER DUCT COPPER | 3.186
cable bus duct cable bus duct 1200AMP FEEDER DUCT ALUMINUM | 3.186
cable bus duct cable bus duct 1200AMP PLUG - IN DUCT COPPER | 3.186
cable bus duct cable bus duct 1200AMP PLUG - IN DUCT ALUMINUM | 3.186
cable bus duct cable bus duct 1350AMP FEEDER DUCT COPPER | 3.908
cable bus duct cable bus duct 1350AMP FEEDER DUCT ALUMINUM | 3.908
cable bus duct cable bus duct 1350AMP PLUG - IN DUCT COPPER | 3.908
cable bus duct cable bus duct 1350AMP PLUG - IN DUCT ALUMINUM | 3.908
cable bus duct cable bus duct 1350AMP FEEDER DUCT COPPER | 3.352
cable bus duct cable bus duct 1350AMP FEEDER DUCT ALUMINUM | 3.352
cable bus duct cable bus duct 1350AMP PLUG - IN DUCT COPPER | 3.352
cable bus duct cable bus duct 1350AMP PLUG - IN DUCT ALUMINUM | 3.352
cable bus duct cable bus duct 1600AMP FEEDER DUCT COPPER | 4.185
cable bus duct cable bus duct 1600AMP FEEDER DUCT ALUMINUM | 4.185
cable bus duct cable bus duct 1600AMP PLUG - IN DUCT COPPER | 4.185
cable bus duct cable bus duct 1600AMP PLUG - IN DUCT ALUMINUM | 4.185
cable bus duct cable bus duct 1600AMP FEEDER DUCT COPPER | 3.63
cable bus duct cable bus duct 1600AMP FEEDER DUCT ALUMINUM | 3.63
cable bus duct cable bus duct 1600AMP PLUG - IN DUCT COPPER | 3.63
cable bus duct cable bus duct 1600AMP PLUG - IN DUCT ALUMINUM | 3.63
cable bus duct cable bus duct 2000AMP FEEDER DUCT COPPER | 4.954
cable bus duct cable bus duct 2000AMP FEEDER DUCT ALUMINUM | 4.954
cable bus duct cable bus duct 2000AMP PLUG - IN DUCT COPPER | 4.954
cable bus duct cable bus duct 2000AMP PLUG - IN DUCT ALUMINUM | 4.954
cable bus duct cable bus duct 2000AMP FEEDER DUCT COPPER | 4.185
cable bus duct cable bus duct 2000AMP FEEDER DUCT ALUMINUM | 4.185
cable bus duct cable bus duct 2000AMP PLUG - IN DUCT COPPER | 4.185
cable bus duct cable bus duct 2000AMP PLUG - IN DUCT ALUMINUM | 4.185
cable bus duct cable bus duct 2500AMP FEEDER DUCT COPPER | 5.831
cable bus duct cable bus duct 2500AMP FEEDER DUCT ALUMINUM | 5.831
cable bus duct cable bus duct 2500AMP PLUG - IN DUCT COPPER | 5.831
cable bus duct cable bus duct 2500AMP PLUG - IN DUCT ALUMINUM | 5.831
cable bus duct cable bus duct 2500AMP FEEDER DUCT COPPER | 4.954
cable bus duct cable bus duct 2500AMP FEEDER DUCT ALUMINUM | 4.954
cable bus duct cable bus duct 2500AMP PLUG - IN DUCT COPPER | 4.954
cable bus duct cable bus duct 2500AMP PLUG - IN DUCT ALUMINUM | 4.954
cable bus duct cable bus duct 5000AMP FEEDER DUCT COPPER | 7.044
cable bus duct cable bus duct 5000AMP FEEDER DUCT ALUMINUM | 7.044
cable bus duct cable bus duct 5000AMP PLUG - IN DUCT COPPER | 7.044
cable bus duct cable bus duct 5000AMP PLUG - IN DUCT ALUMINUM | 7.044
cable bus duct cable bus duct 5000AMP FEEDER DUCT COPPER | 6.156
cable bus duct cable bus duct 5000AMP FEEDER DUCT ALUMINUM | 6.156
cable bus duct cable bus duct 5000AMP PLUG - IN DUCT COPPER | 6.156
cable bus duct cable bus duct 5000AMP PLUG - IN DUCT ALUMINUM | 6.156
cable bus duct cable bus duct tarnsformer to swgear 600AMPS, 600VOLTS | 2.526
cable bus duct cable bus duct tarnsformer to swgear 800AMPS, 600VOLTS | 2.886
cable bus duct cable bus duct tarnsformer to swgear 1000AMPS, 600VOLTS | 3.247
cable bus duct cable bus duct tarnsformer to swgear 1200AMPS, 600VOLTS | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1350AMPS, 600VOLTS | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1600AMPS, 600VOLTS | 3.969
cable bus duct cable bus duct tarnsformer to swgear 2000AMPS, 600VOLTS | 4.33
cable bus duct cable bus duct tarnsformer to swgear 2500AMPS, 600VOLTS | 5.051
cable bus duct cable bus duct tarnsformer to swgear 3000AMPS, 600VOLTS | 5.412
cable bus duct cable bus duct tarnsformer to swgear 3200AMPS, 600VOLTS | 5.628
cable bus duct cable bus duct tarnsformer to swgear 4000AMPS, 600VOLTS | 6.494
cable bus duct cable bus duct tarnsformer to swgear 5000AMPS, 600VOLTS | 7.577
cable bus duct cable bus duct tarnsformer to swgear 6300AMPS, 600VOLTS | 9.547
cable bus duct cable bus duct tarnsformer to swgear 600AMPS, 4.16 KV | 2.886
cable bus duct cable bus duct tarnsformer to swgear 800AMPS, 4.16 kV | 3.247
cable bus duct cable bus duct tarnsformer to swgear 1000AMPS, 4.16 kV | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1200AMPS, 4.16 kV | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1350AMPS, 4.16 kV | 3.969
cable bus duct cable bus duct tarnsformer to swgear 1600AMPS, 4.16 kV | 3.969
cable bus duct cable bus duct tarnsformer to swgear 2000AMPS, 4.16 kV | 4.69
cable bus duct cable bus duct tarnsformer to swgear 2500AMPS, 4.16 kV | 5.412
cable bus duct cable bus duct tarnsformer to swgear 3000AMPS, 4.16 kV | 5.773
cable bus duct cable bus duct tarnsformer to swgear 3200AMPS, 4.16 kV | 5.984
cable bus duct cable bus duct tarnsformer to swgear 4000AMPS, 4.16 kV | 6.855
cable bus duct cable bus duct tarnsformer to swgear 5000AMPS, 4.16 kV | 7.938
cable bus duct cable bus duct tarnsformer to swgear 600AMPS, 13.8 KV | 3.247
cable bus duct cable bus duct tarnsformer to swgear 800AMPS, 13.8 kV | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1000AMPS, 13.8 kV | 3.608
cable bus duct cable bus duct tarnsformer to swgear 1200AMPS, 13.8 kV | 3.969
cable bus duct cable bus duct tarnsformer to swgear 1350AMPS, 13.8 kV | 4.33
cable bus duct cable bus duct tarnsformer to swgear 1600AMPS, 13.8 kV | 4.69
cable bus duct cable bus duct tarnsformer to swgear 2000AMPS, 13.8 kV | 5.051
cable bus duct cable bus duct tarnsformer to swgear 2500AMPS, 13.8 kV | 5.773
cable bus duct cable bus duct tarnsformer to swgear 3000AMPS, 13.8 kV | 6.494
cable bus duct cable bus duct tarnsformer to swgear 4000AMPS, 13.8 kV | 7.216
cable bus duct cable bus duct tarnsformer to swgear 5000AMPS, 13.8 kV | 8.659
cable bus duct cable bus duct tarnsformer to swgear 600AMPS, 34.5 KV | 3.608
cable bus duct cable bus duct tarnsformer to swgear 800AMPS, 34.5 kV | 3.969
cable bus duct cable bus duct tarnsformer to swgear 1000AMPS, 34.5 kV | 4.33
cable bus duct cable bus duct tarnsformer to swgear 1200AMPS, 34.5 kV | 5.051
cable bus duct cable bus duct tarnsformer to swgear 1350AMPS, 34.5 kV | 5.051
cable bus duct cable bus duct tarnsformer to swgear 1600AMPS, 34.5 kV | 5.412
cable bus duct cable bus duct tarnsformer to swgear 2000AMPS, 34.5 kV | 6.134
cable bus duct cable bus duct tarnsformer to swgear 2500AMPS, 34.5 kV | 6.494
cable bus duct cable bus duct tarnsformer to swgear 3000AMPS, 34.5 kV | 7.938
cable bus duct cable bus duct tarnsformer to swgear 4000AMPS, 34.5 kV | 9.381
cable bus duct cable bus duct tarnsformer to swgear 5000AMPS, 34.5 kV | 10.824
cable bus duct (ea) cable bus duct elbow 600V 600AMPS, 600VOLTS | 4.4
cable bus duct (ea) cable bus duct elbow 600V 800AMPS, 600VOLTS | 4.84
cable bus duct (ea) cable bus duct elbow 600V 1000AMPS, 600VOLTS | 5.28
cable bus duct (ea) cable bus duct elbow 600V 1200AMPS, 600VOLTS | 5.72
cable bus duct (ea) cable bus duct elbow 600V 1350AMPS, 600VOLTS | 6.16
cable bus duct (ea) cable bus duct elbow 600V 1600AMPS, 600VOLTS | 7.04
cable bus duct (ea) cable bus duct elbow 600V 2000AMPS, 600VOLTS | 8.36
cable bus duct (ea) cable bus duct elbow 600V 2500AMPS, 600VOLTS | 10.12
cable bus duct (ea) cable bus duct elbow 600V 3000AMPS, 600VOLTS | 12.32
cable bus duct (ea) cable bus duct elbow 600V 3200AMPS, 600VOLTS | 12.848
cable bus duct (ea) cable bus duct elbow 600V 4000AMPS, 600VOLTS | 14.96
cable bus duct (ea) cable bus duct elbow 600V 5000AMPS, 600VOLTS | 18.48
cable bus duct (ea) cable bus duct elbow 600V 6300AMPS, 600VOLTS | 23.285
cable bus duct (ea) cable bus duct elbow 4.16kV 600AMPS, 4.16 KV | 4.84
cable bus duct (ea) cable bus duct elbow 4.16kV 800AMPS, 4.16 kV | 5.39
cable bus duct (ea) cable bus duct elbow 4.16kV 1000AMPS, 4.16 kV | 5.83
cable bus duct (ea) cable bus duct elbow 4.16kV 1200AMPS, 4.16 kV | 6.38
cable bus duct (ea) cable bus duct elbow 4.16kV 1350AMPS, 4.16 kV | 6.82
cable bus duct (ea) cable bus duct elbow 4.16kV 1600AMPS, 4.16 kV | 7.7
cable bus duct (ea) cable bus duct elbow 4.16kV 2000AMPS, 4.16 kV | 9.24
cable bus duct (ea) cable bus duct elbow 4.16kV 2500AMPS, 4.16 kV | 11.22
cable bus duct (ea) cable bus duct elbow 4.16kV 3000AMPS, 4.16 kV | 13.53
cable bus duct (ea) cable bus duct elbow 4.16kV 3200AMPS, 4.16 kV | 14.124
cable bus duct (ea) cable bus duct elbow 4.16kV 4000AMPS, 4.16 kV | 16.5
cable bus duct (ea) cable bus duct elbow 4.16kV 5000AMPS, 4.16 kV | 20.35
cable bus duct (ea) cable bus duct elbow 13.8kV 600AMPS, 13.8 KV | 5.39
cable bus duct (ea) cable bus duct elbow 13.8kV 800AMPS, 13.8 kV | 5.94
cable bus duct (ea) cable bus duct elbow 13.8kV 1000AMPS, 13.8 kV | 6.38
cable bus duct (ea) cable bus duct elbow 13.8kV 1200AMPS, 13.8 kV | 6.93
cable bus duct (ea) cable bus duct elbow 13.8kV 1350AMPS, 13.8 kV | 7.48
cable bus duct (ea) cable bus duct elbow 13.8kV 1600AMPS, 13.8 kV | 8.58
cable bus duct (ea) cable bus duct elbow 13.8kV 2000AMPS, 13.8 kV | 10.23
cable bus duct (ea) cable bus duct elbow 13.8kV 2500AMPS, 13.8 kV | 12.21
cable bus duct (ea) cable bus duct elbow 13.8kV 3000AMPS, 13.8 kV | 14.85
cable bus duct (ea) cable bus duct elbow 13.8kV 4000AMPS, 13.8 kV | 18.15
cable bus duct (ea) cable bus duct elbow 13.8kV 5000AMPS, 13.8 kV | 22.33
cable bus duct (ea) cable bus duct elbow 34.5kV 600AMPS, 34.5 KV | 6.93
cable bus duct (ea) cable bus duct elbow 34.5kV 800AMPS, 34.5 kV | 7.7
cable bus duct (ea) cable bus duct elbow 34.5kV 1000AMPS, 34.5 kV | 8.36
cable bus duct (ea) cable bus duct elbow 34.5kV 1200AMPS, 34.5 kV | 9.02
cable bus duct (ea) cable bus duct elbow 34.5kV 1350AMPS, 34.5 kV | 9.79
cable bus duct (ea) cable bus duct elbow 34.5kV 1600AMPS, 34.5 kV | 11
cable bus duct (ea) cable bus duct elbow 34.5kV 2000AMPS, 34.5 kV | 13.31
cable bus duct (ea) cable bus duct elbow 34.5kV 2500AMPS, 34.5 kV | 15.95
cable bus duct (ea) cable bus duct elbow 34.5kV 3000AMPS, 34.5 kV | 19.36
cable bus duct (ea) cable bus duct elbow 34.5kV 4000AMPS, 34.5 kV | 23.54
cable bus duct (ea) cable bus duct elbow 34.5kV 5000AMPS, 34.5 kV | 29.04
cable bus duct (ea) xformer connection 600V 600AMPS, 600VOLTS | 4.4
cable bus duct (ea) xformer connection 600V 800AMPS, 600VOLTS | 4.84
cable bus duct (ea) xformer connection 600V 1000AMPS, 600VOLTS | 5.28
cable bus duct (ea) xformer connection 600V 1200AMPS, 600VOLTS | 5.72
cable bus duct (ea) xformer connection 600V 1350AMPS, 600VOLTS | 6.16
cable bus duct (ea) xformer connection 600V 1600AMPS, 600VOLTS | 7.04
cable bus duct (ea) xformer connection 600V 2000AMPS, 600VOLTS | 8.36
cable bus duct (ea) xformer connection 600V 2500AMPS, 600VOLTS | 9.68
cable bus duct (ea) xformer connection 600V 3000AMPS, 600VOLTS | 12.32
cable bus duct (ea) xformer connection 600V 4000AMPS, 600VOLTS | 14.96
cable bus duct (ea) xformer connection 600V 5000AMPS, 600VOLTS | 18.48
cable bus duct (ea) xformer connection 4.16kV 600AMPS, 4.16 KV | 4.84
cable bus duct (ea) xformer connection 4.16kV 800AMPS, 4.16 kV | 5.39
cable bus duct (ea) xformer connection 4.16kV 1000AMPS, 4.16 kV | 5.83
cable bus duct (ea) xformer connection 4.16kV 1200AMPS, 4.16 kV | 6.38
cable bus duct (ea) xformer connection 4.16kV 1350AMPS, 4.16 kV | 6.82
cable bus duct (ea) xformer connection 4.16kV 1600AMPS, 4.16 kV | 7.81
cable bus duct (ea) xformer connection 4.16kV 2000AMPS, 4.16 kV | 9.24
cable bus duct (ea) xformer connection 4.16kV 2500AMPS, 4.16 kV | 10.67
cable bus duct (ea) xformer connection 4.16kV 3000AMPS, 4.16 kV | 13.53
cable bus duct (ea) xformer connection 4.16kV 3200AMPS, 4.16 kV | 14.124
cable bus duct (ea) xformer connection 4.16kV 4000AMPS, 4.16 kV | 16.5
cable bus duct (ea) xformer connection 4.16kV 5000AMPS, 4.16 kV | 20.35
cable bus duct (ea) xformer connection 13.8kV 600AMPS, 13.8 KV | 5.39
cable bus duct (ea) xformer connection 13.8kV 800AMPS, 13.8 kV | 5.94
cable bus duct (ea) xformer connection 13.8kV 1000AMPS, 13.8 kV | 6.38
cable bus duct (ea) xformer connection 13.8kV 1200AMPS, 13.8 kV | 6.93
cable bus duct (ea) xformer connection 13.8kV 1350AMPS, 13.8 kV | 7.48
cable bus duct (ea) xformer connection 13.8kV 1600AMPS, 13.8 kV | 8.58
cable bus duct (ea) xformer connection 13.8kV 2000AMPS, 13.8 kV | 10.23
cable bus duct (ea) xformer connection 13.8kV 2500AMPS, 13.8 kV | 11.66
cable bus duct (ea) xformer connection 13.8kV 3000AMPS, 13.8 kV | 14.85
cable bus duct (ea) xformer connection 13.8kV 4000AMPS, 13.8 kV | 18.15
cable bus duct (ea) xformer connection 13.8kV 5000AMPS, 13.8 kV | 22.33
cable bus duct (ea) xformer connection 34.5kV 600AMPS, 34.5 KV | 6.93
cable bus duct (ea) xformer connection 34.5kV 800AMPS, 34.5 kV | 7.7
cable bus duct (ea) xformer connection 34.5kV 1000AMPS, 34.5 kV | 8.36
cable bus duct (ea) xformer connection 34.5kV 1200AMPS, 34.5 kV | 9.02
cable bus duct (ea) xformer connection 34.5kV 1350AMPS, 34.5 kV | 9.79
cable bus duct (ea) xformer connection 34.5kV 1600AMPS, 34.5 kV | 11.22
cable bus duct (ea) xformer connection 34.5kV 2000AMPS, 34.5 kV | 13.31
cable bus duct (ea) xformer connection 34.5kV 2500AMPS, 34.5 kV | 15.18
cable bus duct (ea) xformer connection 34.5kV 3000AMPS, 34.5 kV | 19.36
cable bus duct (ea) xformer connection 34.5kV 4000AMPS, 34.5 kV | 23.54
cable bus duct (ea) xformer connection 34.5kV 5000AMPS, 34.5 kV | 29.04
cable bus duct (ea) swgear connection 600V 600AMPS, 600VOLTS | 2.2
cable bus duct (ea) swgear connection 600V 800AMPS, 600VOLTS | 2.64
cable bus duct (ea) swgear connection 600V 1000AMPS, 600VOLTS | 3.08
cable bus duct (ea) swgear connection 600V 1200AMPS, 600VOLTS | 3.52
cable bus duct (ea) swgear connection 600V 1350AMPS, 600VOLTS | 3.96
cable bus duct (ea) swgear connection 600V 1600AMPS, 600VOLTS | 4.4
cable bus duct (ea) swgear connection 600V 2000AMPS, 600VOLTS | 4.84
cable bus duct (ea) swgear connection 600V 2500AMPS, 600VOLTS | 5.28
cable bus duct (ea) swgear connection 600V 3000AMPS, 600VOLTS | 6.16
cable bus duct (ea) swgear connection 600V 4000AMPS, 600VOLTS | 8.8
cable bus duct (ea) swgear connection 600V 5000AMPS, 600VOLTS | 10.56
cable bus duct (ea) swgear connection 4.16kV 600AMPS, 4.16 KV | 2.42
cable bus duct (ea) swgear connection 4.16kV 800AMPS, 4.16 kV | 2.86
cable bus duct (ea) swgear connection 4.16kV 1000AMPS, 4.16 kV | 3.41
cable bus duct (ea) swgear connection 4.16kV 1200AMPS, 4.16 kV | 3.85
cable bus duct (ea) swgear connection 4.16kV 1350AMPS, 4.16 kV | 4.4
cable bus duct (ea) swgear connection 4.16kV 1600AMPS, 4.16 kV | 4.84
cable bus duct (ea) swgear connection 4.16kV 2000AMPS, 4.16 kV | 5.39
cable bus duct (ea) swgear connection 4.16kV 2500AMPS, 4.16 kV | 5.83
cable bus duct (ea) swgear connection 4.16kV 3000AMPS, 4.16 kV | 6.82
cable bus duct (ea) swgear connection 4.16kV 4000AMPS, 4.16 kV | 9.68
cable bus duct (ea) swgear connection 4.16kV 5000AMPS, 4.16 kV | 11.66
cable bus duct (ea) swgear connection 13.8kV 600AMPS, 13.8 KV | 2.75
cable bus duct (ea) swgear connection 13.8kV 800AMPS, 13.8 kV | 3.19
cable bus duct (ea) swgear connection 13.8kV 1000AMPS, 13.8 kV | 3.74
cable bus duct (ea) swgear connection 13.8kV 1200AMPS, 13.8 kV | 4.18
cable bus duct (ea) swgear connection 13.8kV 1350AMPS, 13.8 kV | 4.84
cable bus duct (ea) swgear connection 13.8kV 1600AMPS, 13.8 kV | 5.39
cable bus duct (ea) swgear connection 13.8kV 2000AMPS, 13.8 kV | 5.94
cable bus duct (ea) swgear connection 13.8kV 2500AMPS, 13.8 kV | 17.38
cable bus duct (ea) swgear connection 13.8kV 3000AMPS, 13.8 kV | 18.48
cable bus duct (ea) swgear connection 13.8kV 4000AMPS, 13.8 kV | 21.67
cable bus duct (ea) swgear connection 13.8kV 5000AMPS, 13.8 kV | 12.76
cable bus duct (ea) swgear connection 34.5kV 600AMPS, 34.5 KV | 3.52
cable bus duct (ea) swgear connection 34.5kV 800AMPS, 34.5 kV | 4.18
cable bus duct (ea) swgear connection 34.5kV 1000AMPS, 34.5 kV | 4.95
cable bus duct (ea) swgear connection 34.5kV 1200AMPS, 34.5 kV | 5.5
cable bus duct (ea) swgear connection 34.5kV 1350AMPS, 34.5 kV | 6.38
cable bus duct (ea) swgear connection 34.5kV 1600AMPS, 34.5 kV | 6.93
cable bus duct (ea) swgear connection 34.5kV 2000AMPS, 34.5 kV | 7.7
cable bus duct (ea) swgear connection 34.5kV 2500AMPS, 34.5 kV | 8.36
cable bus duct (ea) swgear connection 34.5kV 3000AMPS, 34.5 kV | 9.79
cable bus duct (ea) swgear connection 34.5kV 4000AMPS, 34.5 kV | 13.86
cable bus duct (ea) swgear connection 34.5kV 5000AMPS, 34.5 kV | 16.61
cable bus duct cable bus duct under floor ducts 155mm W x 60 mm H 1 Compartment | 0.743
cable bus duct cable bus duct under floor ducts 280mm W x 60 mm H 2 Compartment | 0.935
cable bus duct cable bus duct under floor ducts 280mm W x 60 mm H 3 Compartment | 0.99
cable bus duct cable bus duct under floor ducts 405mm W x 60 mm H 3 Compartment | 1.045
cable bus duct (ea) cross juntion box - 155mm W x 60 mm H 1 Compartment | 1.1
cable bus duct (ea) cross juntion box - 280mm W x 60 mm H 2 Compartment | 1.375
cable bus duct (ea) cross juntion box - 280mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) cross juntion box - 405mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) tee juntion box - 155mm W x 60 mm H 1 Compartment | 0.99
cable bus duct (ea) tee juntion box - 280mm W x 60 mm H 2 Compartment | 1.21
cable bus duct (ea) tee juntion box - 280mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) tee juntion box - 405mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) elbow box - 155mm W x 60 mm H 1 Compartment | 0.935
cable bus duct (ea) elbow box - 280mm W x 60 mm H 2 Compartment | 1.1
cable bus duct (ea) elbow box - 280mm W x 60 mm H 3 Compartment | 1.43
cable bus duct (ea) elbow box - 405mm W x 60 mm H 3 Compartment | 1.43
cable bus duct (ea) vertical access box - 155mm W x 60 mm H 1 Compartment | 1.1
cable bus duct (ea) vertical access box - 280mm W x 60 mm H 2 Compartment | 1.32
cable bus duct (ea) vertical access box - 280mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) vertical access box - 405mm W x 60 mm H 3 Compartment | 1.65
cable bus duct (ea) end cap - 155mm W x 60 mm H 1 Compartment | 0.385
cable bus duct (ea) end cap - 280mm W x 60 mm H 2 Compartment | 0.495
cable bus duct (ea) end cap - 405mm W x 60 mm H 3 Compartment | 0.605
cable bus duct (ea) trunking support bracket adjustable type 155mm W x 60 mm H 1 Compartment | 1.65
cable bus duct (ea) trunking support bracket adjustable type 280mm W x 60 mm H 2 Compartment | 2.2
cable bus duct (ea) trunking support bracket adjustable type 405mm W x 60 mm H 3 Compartment | 2.75
cable bus duct (ea) trunking support bracket fixed height 155mm W x 60 mm H 1 Compartment | 1.1
cable bus duct (ea) trunking support bracket fixed height 280mm W x 60 mm H 2 Compartment | 1.65
cable bus duct (ea) trunking support bracket fixed height 405mm W x 60 mm H 3 Compartment | 2.2
cable bus duct (ea) undergound ducts Electrical Manhole Electrical Manhole | 22
cable bus duct (ea) undergound ducts Electrical Handhole Electrical Handhole | 15.4
cable bus duct (ea) undergound ducts Concrete Ductbanks Concrete Ductbanks | 22
Steel Supports unistrut - 40mm x 40mm, Gauge#16 | 0.5
Steel Supports unistrut - 40mm x 40mm, Gauge#14 | 0.6
Steel Supports unistrut - 40mm x 40mm, Gauge#12 | 0.7
Steel Supports angle bar - 25mm x 25mm, 6.5mm T | 0.4
Steel Supports angle bar - 50mm x 50mm, 6.5mm T | 0.79
Steel Supports angle bar - 75mm x 75mm, 6.5mm T | 1.23
Steel Supports channel - 50mm x 100mm, 6.5mm T | 1.7
Steel Supports (others) mild steel plate - Mild Steel Plate | 0.18
Steel Supports (others) threaded rod - 12mm dia | 0.25
Steel Supports (others) threaded rod - 15mm dia | 0.25
Steel Supports (others) threaded rod - 20mm dia | 0.25
Steel Supports (others) expansion bolt - 12mm dia x 25mm L | 0.15
Steel Supports (others) expansion bolt - 12mm dia x 40mm L | 0.15
Steel Supports (others) expansion bolt - 12mm dia x 50mm L | 0.15
Steel Supports (others) expansion bolt - 12mm dia x 75mm L | 0.2
Steel Supports (others) expansion bolt - 15mm dia x 25mm L | 0.15
Steel Supports (others) expansion bolt - 15mm dia x 40mm L | 0.15
Steel Supports (others) expansion bolt - 15mm dia x 50mm L | 0.2
Steel Supports (others) expansion bolt - 15mm dia x 75mm L | 0.25
Steel Supports (others) u-bolt - 1/2" dia. (15mm.) | 0.1
Steel Supports (others) u-bolt - 3/4" dia. (20mm.) | 0.15
Steel Supports (others) u-bolt - 1" dia. (25mm.) | 0.2
Steel Supports (others) u-bolt - 1-1/4" dia. (32mm.) | 0.2
Steel Supports (others) u-bolt - 1-1/2" dia. (38mm.) | 0.25
Steel Supports (others) u-bolt - 2" dia. (50mm.) | 0.25
Steel Supports (others) u-bolt - 2-1/2" dia. (65mm.) | 0.3
Steel Supports (others) u-bolt - 3" dia. (75mm.) | 0.3
Steel Supports (others) u-bolt - 3-1/2" dia. (90mm.) | 0.4
Steel Supports (others) u-bolt - 4" dia. (100mm.) | 0.4
Steel Supports (others) u-bolt - 5" dia. (125mm.) | 0.45
Steel Supports (others) u-bolt - 6" dia. (150mm.) | 0.5
cable fiber optic fiber optic 2 FIBER | 0.052
cable fiber optic fiber optic 4 FIBER | 0.072
cable fiber optic fiber optic 8 FIBER | 0.103
cable fiber optic fiber optic 12 FIBER | 0.124
cable fiber optic fiber optic 24 FIBER | 0.155
cable fiber optic fiber optic 50 FIBER | 0.258
cable fiber optic fiber optic 100 FIBER | 0.309
cable power cable non-armoured 1/C - # 14 ( 1/C - 2.5 sq. mm.) | 0.031
cable power cable non-armoured #12 ( - 3.50 sq. mm.) | 0.036
cable power cable non-armoured #10 ( - 5.50 sq. mm.) | 0.041
cable power cable non-armoured # 8 ( - 8.00 sq. mm.) | 0.052
cable power cable non-armoured # 6 ( - 14.00 sq. mm.) | 0.061
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.072
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.08
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.093
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.105
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.113
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.13
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.145
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.158
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.169
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.178
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.185
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.202
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.217
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.256
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.283
cable power cable non-armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.081
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.085
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.102
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.107
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.118
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.14
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.158
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.17
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.195
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.225
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.245
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.279
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.298
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.314
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.335
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.361
cable power cable non-armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.064
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.074
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.083
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.095
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.108
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.118
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.133
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.147
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.16
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.172
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.185
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.196
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.207
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.233
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.26
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.294
cable power cable non-armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.111
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.132
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.159
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.176
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.196
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.213
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.233
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.25
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.277
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.301
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.328
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.351
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.381
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.402
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.413
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.433
cable power cable non-armoured 1/C - # 8 ( 1/C - 8.00 sq. mm.) | 0.078
cable power cable non-armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.088
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.098
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.108
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.111
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.118
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.125
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.137
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.151
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.168
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.185
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.196
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.209
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.225
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.247
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.287
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.361
cable power cable non-armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.124
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.146
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.17
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.196
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.212
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.232
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.248
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.263
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.288
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.304
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.331
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.355
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.407
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.417
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.433
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.464
cable power cable non-armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.093
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.107
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.118
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.122
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.13
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.136
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.15
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.166
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.184
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.204
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.215
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.23
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.246
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.272
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.316
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.397
cable power cable non-armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.136
cable power cable non-armoured # 4 ( - 22.00 sq. mm.) | 0.161
cable power cable non-armoured # 2 ( - 30.00 sq. mm.) | 0.186
cable power cable non-armoured # 1 ( - 38.00 sq. mm.) | 0.215
cable power cable non-armoured # 1/0 ( - 50.00 sq. mm.) | 0.233
cable power cable non-armoured # 2/0 ( - 60.00 sq. mm.) | 0.254
cable power cable non-armoured # 3/0 ( - 80.00 sq. mm.) | 0.273
cable power cable non-armoured # 4/0 ( -100.00 sq. mm.) | 0.288
cable power cable non-armoured 250 MCM ( -125.00 sq. mm.) | 0.303
cable power cable non-armoured 300 MCM ( -150.00 sq. mm.) | 0.318
cable power cable non-armoured 350 MCM ( -175.00 sq. mm.) | 0.347
cable power cable non-armoured 400 MCM ( -200.00 sq. mm.) | 0.373
cable power cable non-armoured 500 MCM ( -250.00 sq. mm.) | 0.426
cable power cable non-armoured 600 MCM ( -325.00 sq. mm.) | 0.438
cable power cable non-armoured 750 MCM ( -400.00 sq. mm.) | 0.454
cable power cable non-armoured 1000 MCM ( -500.00 sq. mm.) | 0.486
cable power cable non-armoured - | -
cable power cable armoured 1/C - # 14 ( 1/C - 2.5 sq. mm.) | 0.037
cable power cable armoured #12 ( - 3.50 sq. mm.) | 0.043
cable power cable armoured #10 ( - 5.50 sq. mm.) | 0.049
cable power cable armoured # 8 ( - 8.00 sq. mm.) | 0.062
cable power cable armoured # 6 ( - 14.00 sq. mm.) | 0.073
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.087
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.096
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.111
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.126
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.136
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.156
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.174
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.188
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.203
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.214
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.222
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.242
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.261
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.308
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.34
cable power cable armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.098
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.107
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.124
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.134
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.144
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.174
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.196
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.215
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.242
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.28
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.302
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.317
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.338
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.371
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.404
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.47
cable power cable armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.076
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.093
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.099
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.117
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.128
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.141
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.153
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.165
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.176
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.184
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.194
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.203
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.216
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.258
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.311
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.33
cable power cable armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.134
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.165
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.188
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.219
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.233
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.255
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.27
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.28
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.307
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.314
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.343
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.369
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.421
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.458
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.495
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.515
cable power cable armoured - | -
cable power cable armoured 1/C - # 8 ( 1/C - 8.00 sq. mm.) | 0.094
cable power cable armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.105
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.117
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.13
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.133
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.142
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.149
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.164
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.181
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.202
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.222
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.235
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.251
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.27
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.297
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.345
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.433
cable power cable armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.17
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.193
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.208
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.239
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.259
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.283
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.304
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.32
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.352
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.371
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.404
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.434
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.483
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.494
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.525
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.536
cable power cable armoured 1/C - # 6 ( 1/C - 14.00 sq. mm.) | 0.113
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.129
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.142
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.145
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.156
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.164
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.179
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.199
cable power cable armoured 250 MCM ( -125.00 sq. mm.) | 0.221
cable power cable armoured 300 MCM ( -150.00 sq. mm.) | 0.244
cable power cable armoured 350 MCM ( -175.00 sq. mm.) | 0.258
cable power cable armoured 400 MCM ( -200.00 sq. mm.) | 0.276
cable power cable armoured 500 MCM ( -250.00 sq. mm.) | 0.297
cable power cable armoured 600 MCM ( -325.00 sq. mm.) | 0.325
cable power cable armoured 750 MCM ( -400.00 sq. mm.) | 0.379
cable power cable armoured 1000 MCM ( -500.00 sq. mm.) | 0.476
cable power cable armoured 3/C - # 6 ( 3/C - 14.00 sq. mm.) | 0.186
cable power cable armoured # 4 ( - 22.00 sq. mm.) | 0.211
cable power cable armoured # 2 ( - 30.00 sq. mm.) | 0.229
cable power cable armoured # 1 ( - 38.00 sq. mm.) | 0.263
cable power cable armoured # 1/0 ( - 50.00 sq. mm.) | 0.284
cable power cable armoured # 2/0 ( - 60.00 sq. mm.) | 0.311
cable power cable armoured # 3/0 ( - 80.00 sq. mm.) | 0.334
cable power cable armoured # 4/0 ( -100.00 sq. mm.) | 0.352
cable power cable armoured 250 MCM (125.00 sq. mm.) | 0.37
cable power cable armoured 300 MCM (150.00 sq. mm.) | 0.389
cable power cable armoured 350 MCM (175.00 sq. mm.) | 0.423
cable power cable armoured 400 MCM (200.00 sq. mm.) | 0.455
cable power cable armoured 500 MCM (250.00 sq. mm.) | 0.507
cable power cable armoured 600 MCM (325.00 sq. mm.) | 0.519
cable power cable armoured 750 MCM (400.00 sq. mm.) | 0.546
cable power cable armoured 1000 MCM (500.00 sq. mm.) | 0.556
cable control cable non-armoured 1/C - # 8 ( 1/C - 8.00 sq. mm.) | 0.052
cable control cable non-armoured #10 ( - 5.50 sq. mm.) | 0.041
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.036
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.031
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.031
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.029
cable control cable non-armoured 2/C - # 8 ( 2/C - 8.00 sq. mm.) | 0.062
cable control cable non-armoured #10 ( - 5.50 sq. mm.) | 0.052
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.054
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.052
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.037
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.031
cable control cable non-armoured 3/C - # 8 ( 3/C - 8.00 sq. mm.) | 0.067
cable control cable non-armoured #10 ( - 5.50 sq. mm.) | 0.059
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.057
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.046
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.041
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.036
cable control cable non-armoured 4/C - # 8 ( 4/C - 8.00 sq. mm.) | 0.069
cable control cable non-armoured #10 ( - 5.50 sq. mm.) | 0.067
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.065
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.05
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.046
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.041
cable control cable non-armoured 5/C - #10 ( 5/C - 5.50 sq. mm.) | 0.072
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.07
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.056
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.052
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.043
cable control cable non-armoured 6/C - #10 ( 6/C - 5.50 sq. mm.) | 0.078
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.076
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.058
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.054
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.045
cable control cable non-armoured 7/C - #10 ( 7/C - 5.50 sq. mm.) | 0.081
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.079
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.062
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.057
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.046
cable control cable non-armoured 8/C - #10 ( 8/C - 5.50 sq. mm.) | 0.087
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.084
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.066
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.058
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.05
cable control cable non-armoured 9/C - #10 ( 9/C - 5.50 sq. mm.) | 0.093
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.088
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.068
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.059
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.052
cable control cable non-armoured 10/C - #10 (10/C - 5.50 sq. mm.) | 0.098
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.095
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.073
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.062
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.053
cable control cable non-armoured 11/C - #10 (11/C - 5.50 sq. mm.) | 0.106
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.102
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.075
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.064
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.054
cable control cable non-armoured 12/C - #10 (12/C - 5.50 sq. mm.) | 0.111
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.107
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.078
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.067
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.059
cable control cable non-armoured 13/C - #10 (13/C - 5.50 sq. mm.) | 0.115
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.11
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.08
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.069
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.06
cable control cable non-armoured 14/C - #10 (14/C - 5.50 sq. mm.) | 0.119
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.113
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.083
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.072
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.063
cable control cable non-armoured 15/C - #10 (15/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.115
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.085
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.074
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.065
cable control cable non-armoured 16/C - #10 (16/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.118
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.089
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.077
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.068
cable control cable non-armoured 17/C - #10 (17/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.122
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.091
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.078
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.069
cable control cable non-armoured 18/C - #10 (18/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.125
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.094
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.079
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.07
cable control cable non-armoured 19/C - #10 (19/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.126
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.096
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.082
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.072
cable control cable non-armoured 20/C - #10 (20/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.127
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.099
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.088
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.076
cable control cable non-armoured 21/C - #10 (21/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.13
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.101
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.09
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.078
cable control cable non-armoured 22/C - #10 (22/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.133
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.103
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.093
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.08
cable control cable non-armoured 23/C - #10 (23/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.138
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.106
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.095
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.082
cable control cable non-armoured 24/C - #10 (24/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.141
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.108
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.098
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.085
cable control cable non-armoured 25/C - #10 (25/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.144
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.111
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.1
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.088
cable control cable non-armoured 26/C - #10 (26/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.147
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.114
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.105
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.092
cable control cable non-armoured 27/C - #10 (27/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.149
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.118
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.108
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.095
cable control cable non-armoured 28/C - #10 (28/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.152
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.123
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.11
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.097
cable control cable non-armoured 29/C - #10 (29/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.156
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.124
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.113
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.099
cable control cable non-armoured 30/C - #10 (30/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.159
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.129
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.115
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.101
cable control cable non-armoured 31/C - #10 (31/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.162
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.133
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.118
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.103
cable control cable non-armoured 32/C - #10 (32/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.165
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.136
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.121
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.105
cable control cable non-armoured 33/C - #10 (33/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.172
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.14
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.124
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.108
cable control cable non-armoured 34/C - #10 (34/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.175
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.144
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.126
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.11
cable control cable non-armoured 35/C - #10 (35/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.183
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.149
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.129
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.112
cable control cable non-armoured 36/C - #10 (36/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.19
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.152
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.131
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.114
cable control cable non-armoured 37/C - #10 (37/C - 5.50 sq. mm.) | -
cable control cable non-armoured #12 ( - 3.50 sq. mm.) | 0.193
cable control cable non-armoured #14 ( - 2.00 sq. mm.) | 0.157
cable control cable non-armoured #16 ( - 1.25 sq. mm.) | 0.134
cable control cable non-armoured #22 ( - 0.32 sq. mm.) | 0.117
cable control cable non-armoured - | -
cable control cable armoured 1/C - # 8 ( 1/C - 8.00 sq. mm.) | 0.062
cable control cable armoured #10 ( - 5.50 sq. mm.) | 0.049
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.043
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.037
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.037
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.035
cable control cable armoured 2/C - # 8 ( 2/C - 8.00 sq. mm.) | 0.074
cable control cable armoured #10 ( - 5.50 sq. mm.) | 0.067
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.064
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.052
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.044
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.037
cable control cable armoured 3/C - # 8 ( 3/C - 8.00 sq. mm.) | 0.08
cable control cable armoured #10 ( - 5.50 sq. mm.) | 0.07
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.068
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.056
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.049
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.043
cable control cable armoured 4/C - # 8 ( 4/C - 8.00 sq. mm.) | 0.082
cable control cable armoured #10 ( - 5.50 sq. mm.) | 0.08
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.077
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.061
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.056
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.049
cable control cable armoured 5/C - #10 ( 5/C - 5.50 sq. mm.) | 0.087
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.083
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.067
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.062
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.052
cable control cable armoured 6/C - #10 ( 6/C - 5.50 sq. mm.) | 0.094
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.092
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.069
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.064
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.055
cable control cable armoured 7/C - #10 ( 7/C - 5.50 sq. mm.) | 0.098
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.095
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.074
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.068
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.056
cable control cable armoured 8/C - #10 ( 8/C - 5.50 sq. mm.) | 0.104
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.101
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.079
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.064
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.056
cable control cable armoured 9/C - #10 ( 9/C - 5.50 sq. mm.) | 0.111
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.105
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.081
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.07
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.062
cable control cable armoured 10/C - #10 (10/C - 5.50 sq. mm.) | 0.117
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.114
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.088
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.074
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.063
cable control cable armoured 11/C - #10 (11/C - 5.50 sq. mm.) | 0.127
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.123
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.09
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.076
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.064
cable control cable armoured 12/C - #10 (12/C - 5.50 sq. mm.) | 0.133
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.129
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.094
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.08
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.07
cable control cable armoured 13/C - #10 (13/C - 5.50 sq. mm.) | 0.138
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.132
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.096
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.082
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.071
cable control cable armoured 14/C - #10 (14/C - 5.50 sq. mm.) | 0.143
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.136
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.1
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.087
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.075
cable control cable armoured 15/C - #10 (15/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.138
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.102
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.089
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.077
cable control cable armoured 16/C - #10 (16/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.142
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.106
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.093
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.081
cable control cable armoured 17/C - #10 (17/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.145
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.108
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.094
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.082
cable control cable armoured 18/C - #10 (18/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.149
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.112
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.095
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.083
cable control cable armoured 19/C - #10 (19/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.15
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.119
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.099
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.087
cable control cable armoured 20/C - #10 (20/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.152
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.118
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.105
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.091
cable control cable armoured 21/C - #10 (21/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.156
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.121
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.107
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.094
cable control cable armoured 22/C - #10 (22/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.16
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.124
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.111
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.096
cable control cable armoured 23/C - #10 (23/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.166
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.127
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.113
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.099
cable control cable armoured 24/C - #10 (24/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.169
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.13
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.117
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.102
cable control cable armoured 25/C - #10 (25/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.173
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.133
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.119
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.105
cable control cable armoured 26/C - #10 (26/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.176
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.137
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.126
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.11
cable control cable armoured 27/C - #10 (27/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.179
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.142
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.13
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.113
cable control cable armoured 28/C - #10 (28/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.182
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.205
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.132
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.116
cable control cable armoured 29/C - #10 (29/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.186
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.148
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.136
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.118
cable control cable armoured 30/C - #10 (30/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.191
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.155
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.138
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.121
cable control cable armoured 31/C - #10 (31/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.194
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.16
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.142
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.124
cable control cable armoured 32/C - #10 (32/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.198
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.163
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.152
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.126
cable control cable armoured 33/C - #10 (33/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.206
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.168
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.148
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.13
cable control cable armoured 34/C - #10 (34/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.21
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.173
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.15
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.132
cable control cable armoured 35/C - #10 (35/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.22
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.179
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.155
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.135
cable control cable armoured 36/C - #10 (36/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.228
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.182
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.157
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.137
cable control cable armoured 37/C - #10 (37/C - 5.50 sq. mm.) | -
cable control cable armoured #12 ( - 3.50 sq. mm.) | 0.231
cable control cable armoured #14 ( - 2.00 sq. mm.) | 0.187
cable control cable armoured #16 ( - 1.25 sq. mm.) | 0.161
cable control cable armoured #22 ( - 0.32 sq. mm.) | 0.141
cable control cable armoured - | -
cable instrument cable non-shielded, unarmoured 1 Pair | 0.034
cable instrument cable non-shielded, unarmoured 2 Pair | 0.047
cable instrument cable non-shielded, unarmoured 3 Pair | 0.056
cable instrument cable non-shielded, unarmoured 4 Pair | 0.064
cable instrument cable non-shielded, unarmoured 6 Pair | 0.072
cable instrument cable non-shielded, unarmoured 8 Pair | 0.077
cable instrument cable non-shielded, unarmoured 10 Pair | 0.095
cable instrument cable non-shielded, unarmoured 12 Pair | 0.111
cable instrument cable non-shielded, unarmoured 16 Pair | 0.125
cable instrument cable non-shielded, unarmoured 18 Pair | 0.142
cable instrument cable non-shielded, unarmoured 20 Pair | 0.159
cable instrument cable non-shielded, unarmoured 24 Pair | 0.172
cable instrument cable non-shielded, unarmoured 25 Pair | 0.18
cable instrument cable non-shielded, unarmoured 36 Pair | 0.19
cable instrument cable non-shielded, unarmoured 50 Pair | 0.219
cable instrument cable non-shielded, unarmoured 75 Pair | 0.25
cable instrument cable non-shielded, unarmoured 100 Pair | 0.284
cable instrument cable non-shielded, armoured 1 Pair | 0.047
cable instrument cable non-shielded, armoured 2 Pair | 0.064
cable instrument cable non-shielded, armoured 3 Pair | 0.077
cable instrument cable non-shielded, armoured 4 Pair | 0.095
cable instrument cable non-shielded, armoured 6 Pair | 0.111
cable instrument cable non-shielded, armoured 8 Pair | 0.125
cable instrument cable non-shielded, armoured Non - Shielded, Armored ( Cont'n.) | 0
cable instrument cable non-shielded, armoured 10 Pair | 0.142
cable instrument cable non-shielded, armoured 12 Pair | 0.159
cable instrument cable non-shielded, armoured 16 Pair | 0.172
cable instrument cable non-shielded, armoured 18 Pair | 0.19
cable instrument cable non-shielded, armoured 20 Pair | 0.203
cable instrument cable non-shielded, armoured 24 Pair | 0.219
cable instrument cable non-shielded, armoured 25 Pair | 0.227
cable instrument cable non-shielded, armoured 36 Pair | 0.237
cable instrument cable non-shielded, armoured 50 Pair | 0.267
cable instrument cable non-shielded, armoured 75 Pair | 0.298
cable instrument cable non-shielded, armoured 100 Pair | 0.331
cable instrument cable shielded, unarmoured 1 Pair | 0.041
cable instrument cable shielded, unarmoured 2 Pair | 0.047
cable instrument cable shielded, unarmoured 3 Pair | 0.054
cable instrument cable shielded, unarmoured 4 Pair | 0.064
cable instrument cable shielded, unarmoured 6 Pair | 0.083
cable instrument cable shielded, unarmoured 8 Pair | 0.095
cable instrument cable shielded, unarmoured 10 Pair | 0.111
cable instrument cable shielded, unarmoured 12 Pair | 0.125
cable instrument cable shielded, unarmoured 16 Pair | 0.142
cable instrument cable shielded, unarmoured 18 Pair | 0.159
cable instrument cable shielded, unarmoured 20 Pair | 0.172
cable instrument cable shielded, unarmoured 24 Pair | 0.19
cable instrument cable shielded, unarmoured 25 Pair | 0.194
cable instrument cable shielded, unarmoured 36 Pair | 0.203
cable instrument cable shielded, unarmoured 50 Pair | 0.237
cable instrument cable shielded, unarmoured 75 Pair | 0.267
cable instrument cable shielded, unarmoured 100 Pair | 0.298
cable instrument cable shielded, armoured 1 Pair | 0.064
cable instrument cable shielded, armoured 2 Pair | 0.077
cable instrument cable shielded, armoured 3 Pair | 0.095
cable instrument cable shielded, armoured 4 Pair | 0.111
cable instrument cable shielded, armoured 6 Pair | 0.125
cable instrument cable shielded, armoured 8 Pair | 0.142
cable instrument cable shielded, armoured 10 Pair | 0.159
cable instrument cable shielded, armoured 12 Pair | 0.172
cable instrument cable shielded, armoured 16 Pair | 0.19
cable instrument cable shielded, armoured 18 Pair | 0.203
cable instrument cable shielded, armoured 20 Pair | 0.219
cable instrument cable shielded, armoured 24 Pair | 0.237
cable instrument cable shielded, armoured 25 Pair | 0.242
cable instrument cable shielded, armoured 36 Pair | 0.25
cable instrument cable shielded, armoured 50 Pair | 0.284
cable instrument cable shielded, armoured 75 Pair | 0.314
cable instrument cable shielded, armoured 100 Pair | 0.345
cable (splicing & termination) power cable non-armoured # 6 ( 14.00 sq. mm.) | 0.42
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 0.47
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 0.51
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 0.56
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 0.61
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 0.65
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 0.7
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 0.74
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 0.84
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 0.93
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 1.16
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 1.4
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 1.86
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 2.33
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 2.79
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 3.72
cable (splicing & termination) power cable non-armoured 3/C - # 6 ( 14.00 sq. mm.) | 1.17
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 1.3
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 1.43
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 1.56
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 1.69
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 1.82
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 1.95
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 2.08
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 2.34
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 2.6
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 3.03
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 3.46
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 5.19
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 6.5
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 7.78
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 10.38
cable (splicing & termination) power cable non-armoured 1/C - # 6 ( 14.00 sq. mm.) | 1.95
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 2.15
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 2.35
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 2.45
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 2.6
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 2.7
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 2.85
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 3.25
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 3.7
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 4
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 4.2
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 4.6
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 5.1
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 5.6
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 6
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 6.9
cable (splicing & termination) power cable non-armoured 3/C - # 6 ( 14.00 sq. mm.) | 5.45
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 5.9
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 6.2
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 6.4
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 6.95
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 7.2
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 7.8
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 8.4
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 8.8
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 9.2
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 9.6
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 9.7
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 9.9
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 10.1
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 10.3
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 11
cable (splicing & termination) power cable non-armoured 1/C - # 8 ( 8.00 sq. mm.) | 2.75
cable (splicing & termination) power cable non-armoured 1/C - # 6 ( 14.00 sq. mm.) | 3
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 3.26
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 3.49
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 3.72
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 3.95
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 4.15
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 4.42
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 4.65
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 5.12
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 5.35
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 5.58
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 6.05
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 6.51
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 7.1
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 7.91
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 9.3
cable (splicing & termination) power cable non-armoured 3/C - # 6 ( 14.00 sq. mm.) | 6
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 6.51
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 6.98
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 7.44
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 7.91
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 8.37
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 8.84
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 9.3
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 10.23
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 10.7
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 11.16
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 11.63
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 13.02
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 14
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 15.81
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 16.5
cable (splicing & termination) power cable non-armoured 1/C - # 6 ( 14.00 sq. mm.) | 3.3
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 3.59
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 3.84
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 4.09
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 4.35
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 4.56
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 4.86
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 5.11
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 5.63
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 5.88
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 6.13
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 6.65
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 7.16
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 7.81
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 8.7
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 10.23
cable (splicing & termination) power cable non-armoured 3/C - # 6 ( 14.00 sq. mm.) | 6.6
cable (splicing & termination) power cable non-armoured # 4 ( 22.00 sq. mm.) | 7.16
cable (splicing & termination) power cable non-armoured # 2 ( 30.00 sq. mm.) | 7.67
cable (splicing & termination) power cable non-armoured # 1 ( 38.00 sq. mm.) | 8.18
cable (splicing & termination) power cable non-armoured # 1/0 ( 50.00 sq. mm.) | 8.7
cable (splicing & termination) power cable non-armoured # 2/0 ( 60.00 sq. mm.) | 9.2
cable (splicing & termination) power cable non-armoured # 3/0 ( 80.00 sq. mm.) | 9.72
cable (splicing & termination) power cable non-armoured # 4/0 (100.00 sq. mm.) | 10.23
cable (splicing & termination) power cable non-armoured 250 MCM (125.00 sq. mm.) | 11.25
cable (splicing & termination) power cable non-armoured 300 MCM (150.00 sq. mm.) | 11.77
cable (splicing & termination) power cable non-armoured 350 MCM (175.00 sq. mm.) | 12.27
cable (splicing & termination) power cable non-armoured 400 MCM (200.00 sq. mm.) | 12.79
cable (splicing & termination) power cable non-armoured 500 MCM (250.00 sq. mm.) | 14.32
cable (splicing & termination) power cable non-armoured 600 MCM (325.00 sq. mm.) | 15.4
cable (splicing & termination) power cable non-armoured 750 MCM (400.00 sq. mm.) | 17.39
cable (splicing & termination) power cable non-armoured 1000 MCM (500.00 sq. mm.) | 18.15
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 0.52
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 0.56
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 0.62
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 0.68
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 0.72
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 0.77
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 0.81
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 0.92
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 1.03
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 1.28
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 1.54
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 2.05
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 2.56
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 3.07
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 4.09
cable (splicing & termination) power cable armoured 3/C - # 6 ( 14.00 sq. mm.) | 1.26
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 1.4
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 1.54
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 1.67
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 1.81
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 1.95
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 2.09
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 2.23
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 2.51
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 2.79
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 3.26
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 3.72
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 5.58
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 7.3
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 8.37
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 11.16
cable (splicing & termination) power cable armoured 1/C - # 6 ( 14.00 sq. mm.) | 2.6
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 2.75
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 2.9
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 3
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 3.1
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 3.2
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 3.3
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 3.7
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 4.2
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 4.4
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 4.6
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 5
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 5.6
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 6
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 6.5
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 7.4
cable (splicing & termination) power cable armoured 3/C - # 6 ( 14.00 sq. mm.) | 7.1
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 7.6
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 8.05
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 8.25
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 8.5
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 8.8
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 9
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 9.2
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 9.7
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 10.1
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 10.5
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 10.7
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 11
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 11.2
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 11.3
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 13
cable (splicing & termination) power cable armoured 1/C - # 8 ( 8.00 sq. mm.) | 3
cable (splicing & termination) power cable armoured 1/C - # 6 ( 14.00 sq. mm.) | 3.15
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 3.5
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 3.95
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 4.19
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 4.42
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 4.65
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 4.88
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 5.12
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 5.58
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 5.81
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 6.05
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 6.36
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 6.98
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 7.81
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 8.37
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 9.77
cable (splicing & termination) power cable armoured 3/C - # 6 ( 14.00 sq. mm.) | 9.1
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 9.77
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 10.46
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 11.16
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 11.86
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 12.56
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 13.25
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 13.95
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 14.88
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 15.81
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 16.74
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 17.67
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 19.53
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 21
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 23.25
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 26
cable (splicing & termination) power cable armoured 1/C - # 6 ( 14.00 sq. mm.) | 3.45
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 3.85
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 4.35
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 4.6
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 4.85
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 5.1
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 5.35
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 5.65
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 6.15
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 6.4
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 6.65
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 7
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 7.7
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 8.6
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 9.2
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 10.75
cable (splicing & termination) power cable armoured 3/C - # 6 ( 14.00 sq. mm.) | 10
cable (splicing & termination) power cable armoured # 4 ( 22.00 sq. mm.) | 10.75
cable (splicing & termination) power cable armoured # 2 ( 30.00 sq. mm.) | 11.5
cable (splicing & termination) power cable armoured # 1 ( 38.00 sq. mm.) | 12.25
cable (splicing & termination) power cable armoured # 1/0 ( 50.00 sq. mm.) | 13.05
cable (splicing & termination) power cable armoured # 2/0 ( 60.00 sq. mm.) | 13.8
cable (splicing & termination) power cable armoured # 3/0 ( 80.00 sq. mm.) | 14.55
cable (splicing & termination) power cable armoured # 4/0 (100.00 sq. mm.) | 15.35
cable (splicing & termination) power cable armoured 250 MCM (125.00 sq. mm.) | 16.35
cable (splicing & termination) power cable armoured 300 MCM (150.00 sq. mm.) | 17.4
cable (splicing & termination) power cable armoured 350 MCM (175.00 sq. mm.) | 18.4
cable (splicing & termination) power cable armoured 400 MCM (200.00 sq. mm.) | 19.45
cable (splicing & termination) power cable armoured 500 MCM (250.00 sq. mm.) | 21.5
cable (splicing & termination) power cable armoured 600 MCM (325.00 sq. mm.) | 22.5
cable (splicing & termination) power cable armoured 750 MCM (400.00 sq. mm.) | 25
cable (splicing & termination) power cable armoured 1000 MCM (500.00 sq. mm.) | 27
cable (splicing & termination) power cable connectors & lugs # 6 ( 14.00 sq. mm.) | 0.3
cable (splicing & termination) power cable connectors & lugs # 4 ( 22.00 sq. mm.) | 0.4
cable (splicing & termination) power cable connectors & lugs # 2 ( 30.00 sq. mm.) | 0.45
cable (splicing & termination) power cable connectors & lugs # 1 ( 38.00 sq. mm.) | 0.55
cable (splicing & termination) power cable connectors & lugs # 1/0 ( 50.00 sq. mm.) | 0.7
cable (splicing & termination) power cable connectors & lugs # 2/0 ( 60.00 sq. mm.) | 0.8
cable (splicing & termination) power cable connectors & lugs # 3/0 ( 80.00 sq. mm.) | 1
cable (splicing & termination) power cable connectors & lugs # 4/0 (100.00 sq. mm.) | 1.15
cable (splicing & termination) power cable connectors & lugs 250 MCM (125.00 sq. mm.) | 1.4
cable (splicing & termination) power cable connectors & lugs 300 MCM (150.00 sq. mm.) | 1.6
cable (splicing & termination) power cable connectors & lugs 350 MCM (175.00 sq. mm.) | 1.7
cable (splicing & termination) power cable connectors & lugs 400 MCM (200.00 sq. mm.) | 1.8
cable (splicing & termination) power cable connectors & lugs 500 MCM (250.00 sq. mm.) | 2.1
cable (splicing & termination) power cable connectors & lugs 500 MCM (250.00 sq. mm.) | 2.1
cable (splicing & termination) power cable connectors & lugs 600 MCM (300.00 sq. mm.) | 2.75
cable (splicing & termination) power cable connectors & lugs 750 MCM (375.00 sq. mm.) | 3.15
cable (splicing & termination) power cable connectors & lugs 1000 MCM (500.00 sq. mm.) | 3.6
cable (splicing & termination) power cable connectors & lugs - | -
cable (splicing & termination) motor connections non-hazardous (480 volts) 0 - 10 HP | 2.65
cable (splicing & termination) motor connections non-hazardous (480 volts) - 15 HP | 2.65
cable (splicing & termination) motor connections non-hazardous (480 volts) - 20 HP | 3.25
cable (splicing & termination) motor connections non-hazardous (480 volts) 25 - 30 HP | 3.25
cable (splicing & termination) motor connections non-hazardous (480 volts) - 40 HP | 4.2
cable (splicing & termination) motor connections non-hazardous (480 volts) 50 - 60 HP | 5.45
cable (splicing & termination) motor connections non-hazardous (480 volts) - 75 HP | 6.75
cable (splicing & termination) motor connections non-hazardous (480 volts) - 100 HP | 7.2
cable (splicing & termination) motor connections non-hazardous (480 volts) - 125 HP | 7.2
cable (splicing & termination) motor connections non-hazardous (480 volts) - 150 HP | 9.8
cable (splicing & termination) motor connections non-hazardous (480 volts) - 200 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (480 volts) - 250 HP | 15.7
cable (splicing & termination) motor connections hazardous (480 volts) 0 - 10 HP | 4.6
cable (splicing & termination) motor connections hazardous (480 volts) - 15 HP | 4.6
cable (splicing & termination) motor connections hazardous (480 volts) - 20 HP | 5.35
cable (splicing & termination) motor connections hazardous (480 volts) 25 - 30 HP | 5.35
cable (splicing & termination) motor connections hazardous (480 volts) - 40 HP | 7.4
cable (splicing & termination) motor connections hazardous (480 volts) 50 - 60 HP | 8.7
cable (splicing & termination) motor connections hazardous (480 volts) - 75 HP | 10.5
cable (splicing & termination) motor connections hazardous (480 volts) - 100 HP | 11.5
cable (splicing & termination) motor connections hazardous (480 volts) - 125 HP | 11.5
cable (splicing & termination) motor connections hazardous (480 volts) - 150 HP | 16.9
cable (splicing & termination) motor connections hazardous (480 volts) - 200 HP | 16.9
cable (splicing & termination) motor connections hazardous (480 volts) - 250 HP | 19.5
cable (splicing & termination) motor connections hazardous (480 volts) - | -
cable (splicing & termination) motor connections non-hazardous (2300 volts) 100 - 300 HP | 7.2
cable (splicing & termination) motor connections non-hazardous (2300 volts) 350 - 550 HP | 9.8
cable (splicing & termination) motor connections non-hazardous (2300 volts) 600 - 900 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (2300 volts) - 1000 HP | 15.7
cable (splicing & termination) motor connections hazardous (2300 volts) 100 - 300 HP | 11.5
cable (splicing & termination) motor connections hazardous (2300 volts) 350 - 550 HP | 14
cable (splicing & termination) motor connections hazardous (2300 volts) 600 - 900 HP | 16.9
cable (splicing & termination) motor connections hazardous (2300 volts) - 1000 HP | 19.5
cable (splicing & termination) motor connections hazardous (2300 volts) - | -
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 450 HP | 7.2
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 500 HP | 7.2
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 550 HP | 8.8
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 600 HP | 8.8
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 650 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 700 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 750 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 800 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 900 HP | 12.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 1000 HP | 15.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 1200 HP | 15.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 1400 HP | 18.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 1500 HP | 18.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 2000 HP | 18.7
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 3000 HP | 21.2
cable (splicing & termination) motor connections non-hazardous (4160 volts) - 4000 HP | 26.2
cable (splicing & termination) control cables non-armoured 1/C - # 8 ( 8.00 sq. mm.) | 0.37
cable (splicing & termination) control cables non-armoured #10 ( 5.50 sq. mm.) | 0.33
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 0.28
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 0.2
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 0.18
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.15
cable (splicing & termination) control cables non-armoured 2/C - # 8 ( 8.00 sq. mm.) | 0.71
cable (splicing & termination) control cables non-armoured #10 ( 5.50 sq. mm.) | 0.65
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 0.59
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 0.51
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 0.45
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.3
cable (splicing & termination) control cables non-armoured 3/C - # 8 ( 8.00 sq. mm.) | 1.05
cable (splicing & termination) control cables non-armoured #10 ( 5.50 sq. mm.) | 0.97
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 0.9
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 0.82
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 0.73
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.5
cable (splicing & termination) control cables non-armoured 4/C - # 8 ( 8.00 sq. mm.) | 1.4
cable (splicing & termination) control cables non-armoured #10 ( 5.50 sq. mm.) | 1.05
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 0.98
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 0.95
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 0.85
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.68
cable (splicing & termination) control cables non-armoured 5/C - #10 ( 5.50 sq. mm.) | 1.25
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 1.16
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 1.05
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 0.93
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.75
cable (splicing & termination) control cables non-armoured 6/C - #10 ( 5.50 sq. mm.) | 1.45
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 1.39
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 1.25
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 1.1
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 0.89
cable (splicing & termination) control cables non-armoured 7/C - #10 ( 5.50 sq. mm.) | 1.84
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 1.62
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 1.46
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 1.29
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.05
cable (splicing & termination) control cables non-armoured 8/C - #10 ( 5.50 sq. mm.) | 1.95
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 1.85
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 1.67
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 1.48
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.2
cable (splicing & termination) control cables non-armoured 9/C - #10 ( 5.50 sq. mm.) | 2.2
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 2.08
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 1.88
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 1.67
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.35
cable (splicing & termination) control cables non-armoured 10/C - #10 ( 5.50 sq. mm.) | 2.43
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 2.31
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 2.09
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 1.86
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.5
cable (splicing & termination) control cables non-armoured 11/C - #10 ( 5.50 sq. mm.) | 2.69
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 2.57
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 2.32
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 2.1
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.67
cable (splicing & termination) control cables non-armoured 12/C - #10 ( 5.50 sq. mm.) | 2.98
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 2.86
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 2.58
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 2.37
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 1.86
cable (splicing & termination) control cables non-armoured 13/C - #10 ( 5.50 sq. mm.) | 3.3
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 3.18
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 2.87
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 2.67
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 2.07
cable (splicing & termination) control cables non-armoured 14/C - #10 ( 5.50 sq. mm.) | 3.65
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 3.54
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 3.19
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 3
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 2.3
cable (splicing & termination) control cables non-armoured 15/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 3.94
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 3.55
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 3.37
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 2.55
cable (splicing & termination) control cables non-armoured 16/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 4.38
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 3.95
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 3.79
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 2.83
cable (splicing & termination) control cables non-armoured 17/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 4.87
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 4.4
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 4.26
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 3.14
cable (splicing & termination) control cables non-armoured 18/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 5.41
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 4.9
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 4.79
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 3.48
cable (splicing & termination) control cables non-armoured 19/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 6
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 5.47
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 5.39
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 3.86
cable (splicing & termination) control cables non-armoured 20/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 6.3
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 5.74
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 5.65
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 4.05
cable (splicing & termination) control cables non-armoured 21/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 6.61
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 6.03
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 5.93
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 4.25
cable (splicing & termination) control cables non-armoured 22/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 6.94
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 6.33
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 6.22
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 4.46
cable (splicing & termination) control cables non-armoured 23/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 7.29
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 6.65
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 6.53
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 4.68
cable (splicing & termination) control cables non-armoured 24/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 7.65
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 6.98
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 6.85
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 4.91
cable (splicing & termination) control cables non-armoured 25/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 8.03
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 7.33
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 7.19
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 5.15
cable (splicing & termination) control cables non-armoured 26/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 8.43
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 7.69
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 7.55
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 5.4
cable (splicing & termination) control cables non-armoured 27/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 8.85
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 8.07
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 7.93
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 5.67
cable (splicing & termination) control cables non-armoured 28/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 9.29
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 8.47
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 8.32
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 5.95
cable (splicing & termination) control cables non-armoured 29/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 9.75
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 8.89
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 8.32
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 5.95
cable (splicing & termination) control cables non-armoured 30/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 10.14
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 9.24
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 8.65
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 6.19
cable (splicing & termination) control cables non-armoured 31/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 10.54
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 9.6
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 8.99
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 6.43
cable (splicing & termination) control cables non-armoured 32/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 10.96
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 9.98
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 9.35
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 6.68
cable (splicing & termination) control cables non-armoured 33/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 11.4
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 10.38
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 9.22
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 6.95
cable (splicing & termination) control cables non-armoured 34/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 11.74
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 10.69
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 10.01
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 7.15
cable (splicing & termination) control cables non-armoured 35/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 12.09
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 11.01
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 10.31
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 7.36
cable (splicing & termination) control cables non-armoured 36/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 12.45
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 11.34
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 10.61
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 7.58
cable (splicing & termination) control cables non-armoured 37/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables non-armoured #12 ( 3.50 sq. mm.) | 12.82
cable (splicing & termination) control cables non-armoured #14 ( 2.00 sq. mm.) | 11.68
cable (splicing & termination) control cables non-armoured #16 ( 1.25 sq. mm.) | 10.93
cable (splicing & termination) control cables non-armoured #22 ( 0.32 sq. mm.) | 7.8
cable (splicing & termination) control cables non-armoured - | -
cable (splicing & termination) control cables armoured 1/C - # 8 ( 8.00 sq. mm.) | 0.44
cable (splicing & termination) control cables armoured #10 ( 5.50 sq. mm.) | 0.39
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 0.33
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 0.24
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 0.21
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.18
cable (splicing & termination) control cables armoured 2/C - # 8 ( 8.00 sq. mm.) | 0.85
cable (splicing & termination) control cables armoured #10 ( 5.50 sq. mm.) | 0.78
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 0.71
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 0.61
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 0.54
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.36
cable (splicing & termination) control cables armoured 3/C - # 8 ( 8.00 sq. mm.) | 1.26
cable (splicing & termination) control cables armoured #10 ( 5.50 sq. mm.) | 1.16
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 1.08
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 0.98
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 0.87
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.6
cable (splicing & termination) control cables armoured 4/C - # 8 ( 8.00 sq. mm.) | 1.62
cable (splicing & termination) control cables armoured #10 ( 5.50 sq. mm.) | 1.22
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 1.14
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 1.1
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 0.85
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.79
cable (splicing & termination) control cables armoured 5/C - #10 ( 5.50 sq. mm.) | 1.41
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 1.31
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 1.18
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.05
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.85
cable (splicing & termination) control cables armoured 6/C - #10 ( 5.50 sq. mm.) | 1.61
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 1.55
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 1.39
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.22
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 0.99
cable (splicing & termination) control cables armoured 7/C - #10 ( 5.50 sq. mm.) | 2.02
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 1.78
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 1.6
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.42
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 1.15
cable (splicing & termination) control cables armoured 8/C - #10 ( 5.50 sq. mm.) | 2.11
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 2
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 1.81
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.6
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 1.3
cable (splicing & termination) control cables armoured 9/C - #10 ( 5.50 sq. mm.) | 2.37
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 2.23
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 2.02
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.8
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 1.45
cable (splicing & termination) control cables armoured 10/C - #10 ( 5.50 sq. mm.) | 2.6
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 2.47
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 2.23
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 1.98
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 1.6
cable (splicing & termination) control cables armoured 11/C - #10 ( 5.50 sq. mm.) | 2.85
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 2.73
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 2.46
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 2.23
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 1.77
cable (splicing & termination) control cables armoured 12/C - #10 ( 5.50 sq. mm.) | 3.23
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 3.1
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 2.79
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 2.56
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 2.01
cable (splicing & termination) control cables armoured 13/C - #10 ( 5.50 sq. mm.) | 3.55
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 3.42
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 3.09
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 2.87
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 2.22
cable (splicing & termination) control cables armoured 14/C - #10 ( 5.50 sq. mm.) | 3.91
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 3.79
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 3.42
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 3.21
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 2.46
cable (splicing & termination) control cables armoured 15/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 4.19
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 3.78
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 3.58
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 2.71
cable (splicing & termination) control cables armoured 16/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 4.65
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 4.2
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 4.03
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 3
cable (splicing & termination) control cables armoured 17/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 5.15
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 4.65
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 4.51
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 3.32
cable (splicing & termination) control cables armoured 18/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 5.71
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 5.17
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 5.05
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 3.67
cable (splicing & termination) control cables armoured 19/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 6.32
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 5.75
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 5.67
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 4.06
cable (splicing & termination) control cables armoured 20/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 6.61
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 6.03
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 5.93
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 4.25
cable (splicing & termination) control cables armoured 21/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 6.93
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 6.32
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 6.21
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 4.45
cable (splicing & termination) control cables armoured 22/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 7.35
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 6.7
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 6.59
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 4.73
cable (splicing & termination) control cables armoured 23/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 7.7
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 7.03
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 6.9
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 4.95
cable (splicing & termination) control cables armoured 24/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 8.07
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 7.36
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 7.22
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 5.18
cable (splicing & termination) control cables armoured 25/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 8.45
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 7.72
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 7.57
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 5.42
cable (splicing & termination) control cables armoured 26/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 8.86
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 8.09
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 7.94
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 5.68
cable (splicing & termination) control cables armoured 27/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 9.29
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 8.47
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 8.32
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 5.95
cable (splicing & termination) control cables armoured 28/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 9.72
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 8.86
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 8.71
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 6.22
cable (splicing & termination) control cables armoured 29/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 10.2
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 9.3
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 8.7
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 6.22
cable (splicing & termination) control cables armoured 30/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 10.58
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 9.64
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 9.03
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 6.46
cable (splicing & termination) control cables armoured 31/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 10.99
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 10
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 9.37
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 6.7
cable (splicing & termination) control cables armoured 32/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 11.52
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 10.49
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 9.83
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 7.02
cable (splicing & termination) control cables armoured 33/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 11.96
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 10.9
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 10.2
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 7.3
cable (splicing & termination) control cables armoured 34/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 12.3
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 11.2
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 10.49
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 7.49
cable (splicing & termination) control cables armoured 35/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 12.65
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 11.52
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 10.79
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 7.7
cable (splicing & termination) control cables armoured 36/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 13.03
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 11.87
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 11.1
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 7.93
cable (splicing & termination) control cables armoured 37/C - #10 ( 5.50 sq. mm.) | -
cable (splicing & termination) control cables armoured #12 ( 3.50 sq. mm.) | 13.4
cable (splicing & termination) control cables armoured #14 ( 2.00 sq. mm.) | 12.21
cable (splicing & termination) control cables armoured #16 ( 1.25 sq. mm.) | 11.43
cable (splicing & termination) control cables armoured #22 ( 0.32 sq. mm.) | 8.15
cable (splicing & termination) instrument cables non-shielded,unarmoured 1 Pair | 0.5
cable (splicing & termination) instrument cables non-shielded,unarmoured 2 Pair | 0.93
cable (splicing & termination) instrument cables non-shielded,unarmoured 3 Pair | 1.4
cable (splicing & termination) instrument cables non-shielded,unarmoured 4 Pair | 1.86
cable (splicing & termination) instrument cables non-shielded,unarmoured 6 Pair | 2.8
cable (splicing & termination) instrument cables non-shielded,unarmoured 8 Pair | 3.75
cable (splicing & termination) instrument cables non-shielded,unarmoured 10 Pair | 4.65
cable (splicing & termination) instrument cables non-shielded,unarmoured 12 Pair | 5.6
cable (splicing & termination) instrument cables non-shielded,unarmoured 16 Pair | 7.45
cable (splicing & termination) instrument cables non-shielded,unarmoured 18 Pair | 8.4
cable (splicing & termination) instrument cables non-shielded,unarmoured 20 Pair | 9.3
cable (splicing & termination) instrument cables non-shielded,unarmoured 24 Pair | 11.2
cable (splicing & termination) instrument cables non-shielded,unarmoured 25 Pair | 11.65
cable (splicing & termination) instrument cables non-shielded,unarmoured 36 Pair | 16.75
cable (splicing & termination) instrument cables non-shielded,unarmoured 50 Pair | 23.25
cable (splicing & termination) instrument cables non-shielded,unarmoured 75 Pair | 34.5
cable (splicing & termination) instrument cables non-shielded,unarmoured 100 Pair | 46.5
cable (splicing & termination) instrument cables non-shielded,armoured 1 Pair | 0.7
cable (splicing & termination) instrument cables non-shielded,armoured 2 Pair | 1.2
cable (splicing & termination) instrument cables non-shielded,armoured 3 Pair | 1.65
cable (splicing & termination) instrument cables non-shielded,armoured 4 Pair | 2.1
cable (splicing & termination) instrument cables non-shielded,armoured 6 Pair | 3.05
cable (splicing & termination) instrument cables non-shielded,armoured 8 Pair | 3.95
cable (splicing & termination) instrument cables non-shielded,armoured 10 Pair | 4.9
cable (splicing & termination) instrument cables non-shielded,armoured 12 Pair | 5.85
cable (splicing & termination) instrument cables non-shielded,armoured 16 Pair | 7.7
cable (splicing & termination) instrument cables non-shielded,armoured 18 Pair | 8.6
cable (splicing & termination) instrument cables non-shielded,armoured 20 Pair | 9.6
cable (splicing & termination) instrument cables non-shielded,armoured 24 Pair | 11.4
cable (splicing & termination) instrument cables non-shielded,armoured 25 Pair | 11.85
cable (splicing & termination) instrument cables non-shielded,armoured 36 Pair | 17.45
cable (splicing & termination) instrument cables non-shielded,armoured 50 Pair | 23.5
cable (splicing & termination) instrument cables non-shielded,armoured 75 Pair | 35.1
cable (splicing & termination) instrument cables non-shielded,armoured 100 Pair | 46.75
cable (splicing & termination) instrument cables shielded,unarmoured 1 Pair | 0.7
cable (splicing & termination) instrument cables shielded,unarmoured 2 Pair | 1.4
cable (splicing & termination) instrument cables shielded,unarmoured 3 Pair | 2.1
cable (splicing & termination) instrument cables shielded,unarmoured 4 Pair | 2.8
cable (splicing & termination) instrument cables shielded,unarmoured 6 Pair | 4.2
cable (splicing & termination) instrument cables shielded,unarmoured 8 Pair | 5.6
cable (splicing & termination) instrument cables shielded,unarmoured 10 Pair | 6.2
cable (splicing & termination) instrument cables shielded,unarmoured 12 Pair | 8.4
cable (splicing & termination) instrument cables shielded,unarmoured 16 Pair | 11.2
cable (splicing & termination) instrument cables shielded,unarmoured 18 Pair | 12.6
cable (splicing & termination) instrument cables shielded,unarmoured 20 Pair | 13.95
cable (splicing & termination) instrument cables shielded,unarmoured 24 Pair | 16.75
cable (splicing & termination) instrument cables shielded,unarmoured 25 Pair | 17.45
cable (splicing & termination) instrument cables shielded,unarmoured 36 Pair | 25.15
cable (splicing & termination) instrument cables shielded,unarmoured 50 Pair | 34.45
cable (splicing & termination) instrument cables shielded,unarmoured 75 Pair | 52.35
cable (splicing & termination) instrument cables shielded,unarmoured 100 Pair | 69.75
cable (splicing & termination) instrument cables shielded,armoured 1 Pair | 0.95
cable (splicing & termination) instrument cables shielded,armoured 2 Pair | 1.65
cable (splicing & termination) instrument cables shielded,armoured 3 Pair | 2.35
cable (splicing & termination) instrument cables shielded,armoured 4 Pair | 3.05
cable (splicing & termination) instrument cables shielded,armoured 6 Pair | 4.45
cable (splicing & termination) instrument cables shielded,armoured 8 Pair | 5.85
cable (splicing & termination) instrument cables shielded,armoured 10 Pair | 6.75
cable (splicing & termination) instrument cables shielded,armoured 12 Pair | 8.6
cable (splicing & termination) instrument cables shielded,armoured 16 Pair | 11.4
cable (splicing & termination) instrument cables shielded,armoured 18 Pair | 12.8
cable (splicing & termination) instrument cables shielded,armoured 20 Pair | 14.2
cable (splicing & termination) instrument cables shielded,armoured 24 Pair | 17
cable (splicing & termination) instrument cables shielded,armoured 25 Pair | 17.7
cable (splicing & termination) instrument cables shielded,armoured 36 Pair | 25.35
cable (splicing & termination) instrument cables shielded,armoured 50 Pair | 34.65
cable (splicing & termination) instrument cables shielded,armoured 75 Pair | 52.55
cable (splicing & termination) instrument cables shielded,armoured 100 Pair | 70
cable (splicing & termination) cable glands explosion proof 1/2" dia. ( 15 mm ) | 1.5
cable (splicing & termination) cable glands explosion proof 3/4" dia. ( 20 mm ) | 1.75
cable (splicing & termination) cable glands explosion proof 1" dia. ( 25 mm ) | 2
cable (splicing & termination) cable glands explosion proof 1- 1/4" dia. ( 32 mm ) | 2.25
cable (splicing & termination) cable glands explosion proof 1- 1/2" dia. ( 40 mm ) | 2.5
cable (splicing & termination) cable glands explosion proof 2" dia. ( 50 mm ) | 3
cable (splicing & termination) cable glands explosion proof 2- 1/2" dia. ( 65 mm ) | 3.25
cable (splicing & termination) cable glands explosion proof 3" dia. ( 75 mm ) | 3.5
cable (splicing & termination) cable glands explosion proof 3- 1/2" dia. ( 90 mm ) | 4
cable (splicing & termination) cable glands explosion proof 4" dia. ( 100 mm ) | 5
cable (splicing & termination) cable glands ordinary (plastic) 1/2" dia. ( 15 mm ) | 0.5
cable (splicing & termination) cable glands ordinary (plastic) 3/4" dia. ( 20 mm ) | 0.75
cable (splicing & termination) cable glands ordinary (plastic) 1" dia. ( 25 mm ) | 1
cable (splicing & termination) cable glands ordinary (plastic) 1- 1/4" dia. ( 32 mm ) | 1.25
cable (splicing & termination) cable glands ordinary (plastic) 1- 1/2" dia. ( 40 mm ) | 1.5
cable (splicing & termination) cable glands ordinary (plastic) 2" dia. ( 50 mm ) | 1.75
cable (splicing & termination) cable glands ordinary (plastic) 2- 1/2" dia. ( 65 mm ) | 2
cable (splicing & termination) cable glands ordinary (plastic) 3" dia. ( 75 mm ) | 2.5
cable (splicing & termination) cable glands ordinary (plastic) 3- 1/2" dia. ( 90 mm ) | 3
cable (splicing & termination) cable glands ordinary (plastic) 4" dia. ( 100 mm ) | 3.5
junction box explosion proof w/ mounting lugs 6 x 6 x 4 | 2.3
junction box explosion proof w/ mounting lugs 8 x 8 x 4 | 2.9
junction box explosion proof w/ mounting lugs 10 x 10 x 6 | 3.8
junction box explosion proof w/ mounting lugs 12 x 12 x 6 | 4.2
junction box explosion proof w/ mounting lugs 18 x 12 x 6 | 7
junction box explosion proof w/ mounting lugs 18 x 18 x 8 | 9.9
junction box explosion proof w/ mounting lugs 24 x 18 x 8 | 11.8
junction box explosion proof w/ mounting lugs 24 x 24 x 8 | 17.7
junction box explosion proof w/ mounting lugs 30 x 18 x 8 | 18
junction box explosion proof w/ mounting lugs 30 x 24 x 8 | 21
junction box explosion proof w/ mounting lugs 36 x 24 x 8 | 26
junction box explosion proof w/ mounting lugs 36 x 36 x 12 | 30
junction box explosion proof w/ mounting lugs - | -
junction box non-explosion proof octagonal box OCTAGONAL BOX 4" x 4" x 2 1/8 " | 0.3
junction box non-explosion proof utility box UTILITY BOX 2" x 4" x 2 1/8 " | 0.3
junction box non-explosion proof steel NEMA type 1 6 x 6 x 4 | 0.9
junction box non-explosion proof steel NEMA type 1 8 x 8 x 4 | 1.1
junction box non-explosion proof steel NEMA type 1 10 x 10 x 6 | 1.25
junction box non-explosion proof steel NEMA type 1 12 x 12 x 6 | 2
junction box non-explosion proof steel NEMA type 1 18 x 12 x 6 | 2.5
junction box non-explosion proof steel NEMA type 1 18 x 18 x 8 | 2.5
junction box non-explosion proof steel NEMA type 1 24 x 18 x 8 | 3.25
junction box non-explosion proof steel NEMA type 1 24 x 24 x 8 | 3.25
junction box non-explosion proof steel NEMA type 1 30 x 18 x 8 | 3.5
junction box non-explosion proof steel NEMA type 1 30 x 24 x 8 | 3.75
junction box non-explosion proof steel NEMA type 1 36 x 24 x 8 | 4
junction box non-explosion proof steel NEMA type 1 36 x 36 x 12 | 5
junction box cast iron box - 6 x 6 x 4 | 1.5
junction box cast iron box - 8 x 8 x 4 | 2
junction box cast iron box - 10 x 10 x 6 | 2.5
junction box cast iron box - 12 x 12 x 6 | 3
junction box cast iron box - 18 x 12 x 6 | 4
junction box cast iron box - 18 x 18 x 8 | 7
junction box cast iron box - 24 x 18 x 8 | 9
junction box cast iron box - 24 x 24 x 8 | 11
junction box cast iron box - 30 x 18 x 8 | 13
junction box cast iron box - 30 x 24 x 8 | 14
junction box cast iron box - 36 x 24 x 8 | 19
junction box cast iron box - 36 x 36 x 12 | 22
wiring device switches industrial controls Push Button Cntrl Switch, Start Stop | 2.5
wiring device switches industrial controls Push Button Cntrl Switch, Start Stp w/ Pilot Light | 3
wiring device switches industrial controls Push Button Cntrl Switch, Start Stp w/ Sel. Switch | 3
wiring device switches industrial controls Selector Switch | 2
wiring device switches industrial controls Photo Cell Switch | 2
wiring device switches industrial controls Push Button Control Switch, Explosion Proof | 3.5
wiring device switches industrial controls 10A, Single GangTumbler Switch, Explosion Proof | 1.5
wiring device switches industrial controls - | -
wiring device convenience outlet - 20 A, Factory Sealed, Explosion Proof Outlet | 2.5
wiring device special purpose outlet - 60A, Welding Receptacle, Explosion Proof | 4.5
wiring device special purpose outlet - 60A, Welding Receptacle w/ Crkt Bkr, Exp. Proof | 8
wiring device special purpose outlet - - | -
wiring device switches lighting system 10Amp., Single Gang Tumbler Switch | 0.5
wiring device switches lighting system 10Amp., Two Gang Tumbler Switch | 0.6
wiring device switches lighting system 10Amp., Three Gang Tumbler Switch | 0.75
wiring device switches lighting system 10Amp., Three Way Tumbler Switch | 0.75
wiring device switches lighting system 10Amp., Double Pole Tumbler Switch | 1
wiring device switches lighting system 10Amp., Four Way Tumbler Switch | 1
wiring device switches lighting system 10Amp., Single Gang Tumbler Switch, WP | 0.65
wiring device switches lighting system 10Amp., Two Gang Tumbler Switch, WP | 0.75
wiring device switches lighting system 10Amp., Three Gang Tumbler Switch, WP | 0.95
wiring device switches lighting system 10Amp., Three Way Tumbler Switch, WP | 0.95
wiring device switches lighting system Door Switch with Box | 2
wiring device switches lighting system Tumbler Type Dimmer Swich | 0.75
wiring device switches lighting system Rotary Type Dimmer Swich | 1
wiring device convenience outlet - 15Amp., Single Receptacles, NonGrounding Type | 0.4
wiring device convenience outlet - 15Amp., Single Receptacles, Grounding Type | 0.5
wiring device convenience outlet - 15Amp., Duplex Receptacles, Non Grounding Type | 0.5
wiring device convenience outlet - 15Amp., Duplex Receptacles, Grounding Type | 0.65
wiring device convenience outlet - 15Amp., Single Receptacles, NonGrounding, 3 Pole | 0.9
wiring device convenience outlet - 15Amp., Single Receptacles, Grounding, 3 Pole | 1.25
wiring device convenience outlet - 15Amp., Single Receptacles, Non Grdng Type, WP | 0.548
wiring device convenience outlet - 15Amp., Single Receptacles, Grounding Type, WP | 0.65
wiring device convenience outlet - 15Amp., Duplex Receptacles, Non Gring Type, WP | 0.65
wiring device convenience outlet - 15Amp., Duplex Receptacles, Grounding Type, WP | 0.845
wiring device convenience outlet - - | -
wiring device special purpose outlet - 30 Amp ACU Outlet | 0.8
wiring device special purpose outlet - Floor Outlet | 1
wiring device special purpose outlet - - | -
lighting fixtures incandescent lamp surface mounted SURFACE MOUNTED | 1.5
lighting fixtures incandescent lamp ceiling suspended ( pendant ) CEILING SUSPENDED ( PENDANT ) | 2
lighting fixtures incandescent lamp explosion proof EXPLOSION PROOF | 3
lighting fixtures incandescent lamp wall mount WALL MOUNT | 1.6
lighting fixtures incandescent lamp stanchion mount STANCHION MOUNT | 1.8
lighting fixtures incandescent lamp beacon lights BEACON LIGHTS | 4.5
lighting fixtures incandescent lamp obstruction lights, single fixture OBSTRUCTION LIGHTS, SINGLE FIXTURE | 3
lighting fixtures incandescent lamp obstruction lights, double fixture OBSTRUCTION LIGHTS, DOUBLE FIXTURE | 3.6
lighting fixtures incandescent lamp - - | -
Area Floodlight, 25 Watts | 2.5
Area Floodlight, 50 Watts | 2.75
Area Floodlight, 100 Watts | 3
Area Floodlight, 150 Watts | 3.25
lighting fixtures metal hallide lamp flood light Area Floodlight, 250 Watts | 3.5
lighting fixtures metal hallide lamp flood light Area Floodlight, 400 Watts | 4
lighting fixtures metal hallide lamp flood light Area Floodlight, 500 Watts | 4.5
lighting fixtures metal hallide lamp flood light Area Floodlight, 1000 Watts | 7
lighting fixtures metal hallide lamp street light Street Lighting, 250 Watts | 4
lighting fixtures metal hallide lamp street light Street Lighting, 400 Watts | 4
lighting fixtures metal hallide lamp pendant mounted 100 Watts | 2.25
lighting fixtures metal hallide lamp pendant mounted 175 Watts | 2.25
lighting fixtures metal hallide lamp pendant mounted 250 Watts | 2.5
lighting fixtures metal hallide lamp ceiling mounted 100 Watts | 2.25
lighting fixtures metal hallide lamp ceiling mounted 175 Watts | 2.25
lighting fixtures metal hallide lamp ceiling mounted 250 Watts | 2.5
lighting fixtures metal hallide lamp wall mounted 100 Watts | 2
lighting fixtures metal hallide lamp wall mounted 175 Watts | 2
lighting fixtures metal hallide lamp wall mounted 250 Watts | 2.25
lighting fixtures metal hallide lamp stanchion mounted 100 Watts | 2.5
lighting fixtures metal hallide lamp stanchion mounted 175 Watts | 2.5
lighting fixtures metal hallide lamp stanchion mounted 250 Watts | 3
Area Floodlight, 25 Watts | 4
Area Floodlight, 50 Watts | 4.25
Area Floodlight, 100 Watts | 4.5
Area Floodlight, 150 Watts | 4.75
lighting fixtures metal hallide lamp explosion proof Area Floodlight, 250 Watts | 5.25
lighting fixtures metal hallide lamp explosion proof Area Floodlight, 400 Watts | 6
Area Floodlight, 400 Watts | 6
Area Floodlight, 400 Watts | 6
lighting fixtures metal hallide lamp explosion proof Street Lighting, 250 Watts | 6
lighting fixtures metal hallide lamp explosion proof Street Lighting, 400 Watts | 6
lighting fixtures high bay luminaires pendant mounted 250 Watts (Mercury, HPS, Metal Halide) | 3
lighting fixtures high bay luminaires pendant mounted 400 Watts (Mercury, HPS, Metal Halide) | 3.5
lighting fixtures high bay luminaires pendant mounted 1000 Watts (Mercury, HPS, Metal Halide) | 4
lighting fixtures high bay luminaires pendant mounted 250 Watts (Mercury, HPS, Metal Halide) | 2.75
lighting fixtures high bay luminaires pendant mounted 400 Watts (Mercury, HPS, Metal Halide) | 3.5
lighting fixtures high bay luminaires pendant mounted - | -
lighting fixtures flourescent fixtures surface mounted 1 X 20 Watts | 1.75
lighting fixtures flourescent fixtures surface mounted 2 X 20 Watts | 2
lighting fixtures flourescent fixtures surface mounted 3 X 20 Watts | 2.25
lighting fixtures flourescent fixtures surface mounted 1 X 40 Watts | 2.25
lighting fixtures flourescent fixtures surface mounted 2 X 40 Watts | 2.5
lighting fixtures flourescent fixtures surface mounted 3 X 40 Watts | 3
lighting fixtures flourescent fixtures surface mounted 4 X 40 Watts | 3.5
lighting fixtures flourescent fixtures ceiling mounted 1 X 20 Watts | 2.3
lighting fixtures flourescent fixtures ceiling mounted 2 X 20 Watts | 2.5
lighting fixtures flourescent fixtures ceiling mounted 3 X 20 Watts | 2.75
lighting fixtures flourescent fixtures ceiling mounted 1 X 40 Watts | 2.75
lighting fixtures flourescent fixtures ceiling mounted 2 X 40 Watts | 3
lighting fixtures flourescent fixtures ceiling mounted 3 X 40 Watts | 3.25
lighting fixtures flourescent fixtures ceiling mounted 4 X 40 Watts | 3.5
lighting fixtures flourescent fixtures recessed mounted 1 X 20 Watts | 2.5
lighting fixtures flourescent fixtures recessed mounted 2 X 20 Watts | 2.75
lighting fixtures flourescent fixtures recessed mounted 3 X 20 Watts | 3
lighting fixtures flourescent fixtures recessed mounted 1 X 40 Watts | 3
lighting fixtures flourescent fixtures recessed mounted 2 X 40 Watts | 3.25
lighting fixtures flourescent fixtures recessed mounted 3 X 40 Watts | 3.5
lighting fixtures flourescent fixtures recessed mounted 4 X 40 Watts | 3.75
lighting fixtures flourescent fixtures explosion proof 1 X 20 Watts | 2.748
lighting fixtures flourescent fixtures explosion proof 2 X 20 Watts | 3
lighting fixtures flourescent fixtures explosion proof 1 X 40 Watts | 3.553
lighting fixtures flourescent fixtures explosion proof 2 X 40 Watts | 3.75
lighting fixtures flourescent fixtures - - | -
5 FT. HIGH | 3
lighting pole lighting pole lighting pole 10 FT. HIGH | 4
lighting pole lighting pole lighting pole 15 FT. HIGH | 5
lighting pole lighting pole lighting pole 20 FT. HIGH | 5.5
lighting pole lighting pole lighting pole 30 FT. HIGH | 6
lighting pole lighting pole lighting pole 33 FT. HIGH | 6.3
lighting pole lighting pole lighting pole 40 FT. HIGH | 7
50 FT. HIGH | 8.5
60 FT. HIGH | 10
70 FT. HIGH | 11.5
80 FT. HIGH | 13
90 FT. HIGH | 14.5
100 FT. HIGH | 16
100 FT. HIGH | 17.5
100 FT. HIGH | 19
lighting pole lighting pole - - | -
grounding ground well - INSTALL GROUNDWELLS | 4.5
grounding ground well - - | -
grounding copperweld rods - 5/8" DIAMETER X 10 FT. | 2.5
grounding copperweld rods - 3/4" DIAMETER X 10 FT. | 3
grounding copperweld rods - 1" DIAMETER X 10 FT. | 3
grounding copperweld rods - 5/8" GROUND ROD CLAMP | 0.75
grounding copperweld rods - 3/4" GROUND ROD CLAMP | 0.75
grounding copperweld rods bonding jumper BONDING JUMPER | 2.5
grounding copperweld rods lightning terminal LIGHTNING TERMINAL, CONVENTIONAL TYPE | 3
grounding copperweld rods lightning terminal LIGHTNING TERMINAL, IONIZATION TYPE | 4.5
grounding copper grounding bar - 1/4 " T X 1.0 " W COPPER GROUNDING BAR | 0.59
grounding copper grounding bar - 1/4 " T X 1.5 " W COPPER GROUNDING BAR | 0.886
grounding copper grounding bar - 1/4 " T X 2.0 " W COPPER GROUNDING BAR | 1.181
grounding copper grounding bar - 1/4 " T X 2.5 " W COPPER GROUNDING BAR | 1.476
grounding copper grounding bar - 1/4 " T X 3.0 " W COPPER GROUNDING BAR | 1.771
grounding copper grounding bar - 1/2 " T X 1.0 " W COPPER GROUNDING BAR | 2.362
grounding copper grounding bar - 1/2 " T X 1.5 " W COPPER GROUNDING BAR | 2.952
grounding copper grounding bar - 1/2 " T X 2.0 " W COPPER GROUNDING BAR | 3.542
grounding copper grounding bar - 1/2 " T X 2.5 " W COPPER GROUNDING BAR | 4.133
grounding copper grounding bar - 1/2 " T X 3.0 " W COPPER GROUNDING BAR | 4.723
grounding copper grounding bar - - | -
grounding bare copper wire - # 8 ( 8.00 sq. mm.) | 0.06
grounding bare copper wire - # 6 ( 14.00 sq. mm.) | 0.07
grounding bare copper wire - # 4 ( 22.00 sq. mm.) | 0.09
grounding bare copper wire - # 2 ( 30.00 sq. mm.) | 0.105
grounding bare copper wire - # 2/0 ( 60.00 sq. mm.) | 0.14
grounding bare copper wire - # 3/0 ( 80.00 sq. mm.) | 0.15
grounding bare copper wire - # 4/0 (100.00 sq. mm.) | 0.17
grounding bare copper wire - 250 MCM (125.00 sq. mm.) | 0.2
grounding bare copper wire - 500 MCM (250.00 sq. mm.) | 0.25
grounding bare copper wire - - | -
grounding bare copper wire connection exothermic # 2 ( 30.00 sq. mm.) | 1.25
grounding bare copper wire connection exothermic # 1/0 ( 50.00 sq. mm.) | 1.25
grounding bare copper wire connection exothermic # 2/0 ( 60.00 sq. mm.) | 1.25
grounding bare copper wire connection exothermic # 3/0 ( 80.00 sq. mm.) | 1.25
grounding bare copper wire connection exothermic # 4/0 (100.00 sq. mm.) | 1.5
grounding bare copper wire connection exothermic 250 MCM (125.00 sq. mm.) | 1.5
grounding bare copper wire connection exothermic 300 MCM (150.00 sq. mm.) | 2
grounding bare copper wire connection exothermic 400 MCM (200.00 sq. mm.) | 2
grounding bare copper wire connection exothermic 500 MCM (250.00 sq. mm.) | 2.5
grounding bare copper wire connection exothermic 600 MCM (300.00 sq. mm.) | 3
800 MCM (400.00 sq. mm.) | 3.5
grounding bare copper wire connection exothermic - | -
grounding bare copper wire connection compression # 2 ( 30.00 sq. mm.) | 0.65
grounding bare copper wire connection compression # 1/0 ( 50.00 sq. mm.) | 1.1
grounding bare copper wire connection compression # 2/0 ( 60.00 sq. mm.) | 1.2
grounding bare copper wire connection compression # 3/0 ( 80.00 sq. mm.) | 1.35
grounding bare copper wire connection compression # 4/0 (100.00 sq. mm.) | 1.6
grounding bare copper wire connection compression 250 MCM (125.00 sq. mm.) | 1.8
grounding bare copper wire connection compression 300 MCM (150.00 sq. mm.) | 2.05
grounding bare copper wire connection compression 400 MCM (200.00 sq. mm.) | 2.5
grounding bare copper wire connection compression 500 MCM (250.00 sq. mm.) | 3.15
grounding bare copper wire connection compression 600 MCM (300.00 sq. mm.) | 4
800 MCM (400.00 sq. mm.) | 4.5
grounding bare copper wire connection compression - | -
equipment distribution panel board pre-wired/pre-assembled 6 - Breakers, 100 AT MAIN | 4
equipment distribution panel board pre-wired/pre-assembled 12 - Breakers, 100 AT MAIN | 9
equipment distribution panel board pre-wired/pre-assembled 16 - Breakers, 100 AT MAIN | 11
equipment distribution panel board pre-wired/pre-assembled 18 - Breakers, 100 AT MAIN | 14
equipment distribution panel board pre-wired/pre-assembled 24 - Breakers, 100 AT MAIN | 17
equipment distribution panel board pre-wired/pre-assembled 30 - Breakers, 225 AT MAIN | 20
equipment distribution panel board pre-wired/pre-assembled 42 - Breakers, 225 AT MAIN | 28
equipment distribution panel board site wired/ site assembled 12 - Breakers, 100 AT MAIN | 12
equipment distribution panel board site wired/ site assembled 18 - Breakers, 100 AT MAIN | 18
equipment distribution panel board site wired/ site assembled 30 - Breakers, 225 AT MAIN | 24
equipment distribution panel board site wired/ site assembled 42 - Breakers, 225 AT MAIN | 40
equipment circuit braker ECB 30 AMP | 4
equipment circuit braker ECB 60 AMP | 4
equipment circuit braker ECB 100 AMP | 7
equipment circuit braker ECB 125 AMP | 7
equipment circuit braker ECB 150 AMP | 7
equipment circuit braker ECB 200 AMP | 9
equipment circuit braker ECB 225 AMP | 10
equipment circuit braker ECB 250 AMP | 12
equipment circuit braker ECB 400 AMP | 15
equipment circuit braker ECB 600 AMP | 22
equipment circuit braker ECB 800 AMP | 26
equipment circuit braker ECB 1000 AMP | 30
equipment circuit braker ECB 1200 AMP | 34
equipment circuit braker ECB - | -
equipment safety switch - 30 AMP | 4
equipment safety switch - 60 AMP | 4
equipment safety switch - 100 AMP | 6
equipment safety switch - 200 AMP | 8
equipment safety switch - 400 AMP | 12
equipment safety switch - 600 AMP | 20
equipment safety switch - 800 AMP | 24
equipment safety switch - 1000 AMP | 28
equipment safety switch - 1200 AMP | 30
equipment switch gear pre-wired/pre-assembled SWITCHGEARS, L.V., 600V | 30
equipment switch gear pre-wired/pre-assembled SWITCHGEARS, M.V., 5 KV | 40
equipment switch gear pre-wired/pre-assembled SWITCHGEARS, M.V., 15 KV | 46
equipment switch gear site wired/ site assembled SWITCHGEARS, L.V., 600V | 44
equipment switch gear site wired/ site assembled SWITCHGEARS, M.V., 5KV | 54
equipment switch gear site wired/ site assembled SWITCHGEARS, M.V., 15KV | 62
equipment mcc, 480V pre-wired/pre-assembled INSTALL IN PLACE PER VERTICAL SECTION | 30
equipment mcc,2400V pre-wired/pre-assembled INSTALL IN PLACE PER VERTICAL SECTION | 36
equipment mcc,4800V pre-wired/pre-assembled INSTALL IN PLACE PER VERTICAL SECTION | 42
equipment mcc, 480V site wired/ site assembled INSTALL IN PLACE PER VERTICAL SECTION | 30
equipment mcc, 480V site wired/ site assembled SIZE 1 ( 1/2 THRU 10 HP MOTORS ) | 2
equipment mcc, 480V site wired/ site assembled SIZE 2 ( 15 THRU 25 HP MOTORS ) | 2
equipment mcc, 480V site wired/ site assembled SIZE 3 ( 30 THRU 50 HP MOTORS ) | 3
equipment mcc, 480V site wired/ site assembled SIZE 4 ( 60 THRU 100 HP MOTORS ) | 3
equipment mcc, 480V site wired/ site assembled SIZE 5 ( 125 THRU 200 HP MOTORS ) | 4
equipment mcc, 480V site wired/ site assembled SIZE 6 ( 200 THRU 200 HP MOTORS ) | 5
equipment mcc, 480V site wired/ site assembled SIZE 2 ( 15 THRU 25 HP MOTORS ) | 4
equipment mcc, 480V site wired/ site assembled SIZE 3 ( 30 THRU 50 HP MOTORS ) | 5
equipment mcc, 480V site wired/ site assembled SIZE 4 ( 60 THRU 100 HP MOTORS ) | 5
equipment mcc, 480V site wired/ site assembled SIZE 5 ( 125 THRU 200 HP MOTORS ) | 6
equipment mcc, 480V site wired/ site assembled SIZE 6 ( 200 THRU 200 HP MOTORS ) | 6
equipment mcc, 480V site wired/ site assembled SIZE 1 ( 1/2 THRU 10 HP MOTORS ) | 3
equipment mcc, 480V site wired/ site assembled SIZE 2 ( 15 THRU 25 HP MOTORS ) | 3
equipment mcc, 480V site wired/ site assembled SIZE 3 ( 30 THRU 50 HP MOTORS ) | 4
equipment mcc, 480V site wired/ site assembled SIZE 4 ( 60 THRU 100 HP MOTORS ) | 4
equipment mcc, 480V site wired/ site assembled SIZE 5 ( 125 THRU 200 HP MOTORS ) | 5
equipment mcc, 480V site wired/ site assembled SIZE 6 ( 200 THRU 200 HP MOTORS ) | 6
equipment mcc, 480V site wired/ site assembled PER SECTION | 1
equipment mcc, 480V site wired/ site assembled PER SECTION | 1
equipment mcc, 480V site wired/ site assembled PER SECTION | 1
equipment mcc, 480V site wired/ site assembled - | -
equipment mcc,2400V site wired/ site assembled INSTALL IN PLACE PER VERTICAL SECTION | 36
equipment mcc,2400V site wired/ site assembled 200 THRU 400 HP | 8
equipment mcc,2400V site wired/ site assembled 500 THRU 700 HP | 12
equipment mcc,2400V site wired/ site assembled 800 THRU 2500 HP | 18
equipment mcc,2400V site wired/ site assembled PER SECTION | 1
equipment mcc,2400V site wired/ site assembled PER SECTION | 1
equipment mcc,4800V site wired/ site assembled INSTALL IN PLACE PER VERTICAL SECTION | 42
equipment mcc,4800V site wired/ site assembled 200 THRU 400 HP | 8
equipment mcc,4800V site wired/ site assembled 500 THRU 700 HP | 12
equipment mcc,4800V site wired/ site assembled 800 THRU 2500 HP | 18
equipment mcc,4800V site wired/ site assembled PER SECTION | 1
equipment mcc,4800V site wired/ site assembled PER SECTION | 1
equipment motor starter enclosed, magnetic non reverse 2 - HP, NEMA SIZE 00 | 3
equipment motor starter enclosed, magnetic non reverse 3 - 5 HP, NEMA SIZE 0 | 4
equipment motor starter enclosed, magnetic non reverse 7.5 - 10 HP, NEMA SIZE 1 | 5
equipment motor starter enclosed, magnetic non reverse 15 - 25 HP, NEMA SIZE 2 | 7
equipment motor starter enclosed, magnetic non reverse 30 - 50 HP, NEMA SIZE 3 | 9
equipment motor starter enclosed, magnetic non reverse 60 - 75 HP, NEMA SIZE 4 | 12
equipment motor starter enclosed, magnetic non reverse 100 HP, NEMA SIZE 4 | 15
equipment motor starter enclosed, magnetic non reverse 200 HP, NEMA SIZE 5 | 20
equipment motor starter enclosed, magnetic reverse 2 - HP, NEMA SIZE 00 | 5
equipment motor starter enclosed, magnetic reverse 3 - 5 HP, NEMA SIZE 0 | 6
equipment motor starter enclosed, magnetic reverse 7.5 - 10 HP, NEMA SIZE 1 | 7
equipment motor starter enclosed, magnetic reverse 15 - 25 HP, NEMA SIZE 2 | 9
equipment motor starter enclosed, magnetic reverse 30 - 50 HP, NEMA SIZE 3 | 12
equipment motor starter enclosed, magnetic reverse 60 - 75 HP, NEMA SIZE 4 | 14
equipment motor starter enclosed, magnetic reverse 100 HP, NEMA SIZE 4 | 18
equipment motor starter enclosed, magnetic reverse 200 HP, NEMA SIZE 5 | 24
equipment motor starter enclosed, magnetic non reverse w/ c/b 2 - HP, NEMA SIZE 00 | 4
equipment motor starter enclosed, magnetic non reverse w/ c/b 3 - 5 HP, NEMA SIZE 0 | 5
equipment motor starter enclosed, magnetic non reverse w/ c/b 7.5 - 10 HP, NEMA SIZE 1 | 6
equipment motor starter enclosed, magnetic non reverse w/ c/b 15 - 25 HP, NEMA SIZE 2 | 10
equipment motor starter enclosed, magnetic non reverse w/ c/b 30 - 50 HP, NEMA SIZE 3 | 12
equipment motor starter enclosed, magnetic non reverse w/ c/b 60 - 75 HP, NEMA SIZE 4 | 14
equipment motor starter enclosed, magnetic non reverse w/ c/b 100 HP, NEMA SIZE 4 | 18
equipment motor starter enclosed, magnetic non reverse w/ c/b 200 HP, NEMA SIZE 5 | 24
equipment motor starter enclosed, magnetic reverse w/ c/b 2 - HP, NEMA SIZE 00 | 6
equipment motor starter enclosed, magnetic reverse w/ c/b 3 - 5 HP, NEMA SIZE 0 | 7
equipment motor starter enclosed, magnetic reverse w/ c/b 7.5 - 10 HP, NEMA SIZE 1 | 8
equipment motor starter enclosed, magnetic reverse w/ c/b 15 - 25 HP, NEMA SIZE 2 | 12
equipment motor starter enclosed, magnetic reverse w/ c/b 30 - 50 HP, NEMA SIZE 3 | 14
equipment motor starter enclosed, magnetic reverse w/ c/b 60 - 75 HP, NEMA SIZE 4 | 16
equipment motor starter enclosed, magnetic reverse w/ c/b 100 HP, NEMA SIZE 4 | 21
equipment motor starter enclosed, magnetic reverse w/ c/b 200 HP, NEMA SIZE 5 | 28
equipment dry type transformers 1 phase 5 KVA | 12
equipment dry type transformers 1 phase 7.5 KVA | 14
equipment dry type transformers 1 phase 10 KVA | 15
equipment dry type transformers 1 phase 15 KVA | 20
equipment dry type transformers 1 phase 25 KVA | 23
equipment dry type transformers 1 phase 37.5 KVA | 28
equipment dry type transformers 1 phase 50 KVA | 32
equipment dry type transformers 1 phase 75 KVA | 40
equipment dry type transformers 1 phase 100 KVA | 54
equipment dry type transformers 3 phase 6 KVA | 14
equipment dry type transformers 3 phase 9 KVA | 17
equipment dry type transformers 3 phase 15 KVA | 24
equipment dry type transformers 3 phase 30 KVA | 28
equipment dry type transformers 3 phase 45 KVA | 36
equipment dry type transformers 3 phase 75 KVA | 46
equipment dry type transformers 3 phase 112.5 KVA | 60
equipment dry type transformers 3 phase 150 KVA | 80
equipment dry type transformers 3 phase 225 KVA | 94
equipment dry type transformers 3 phase 300 KVA | 106
equipment distribution transformers 1 phase 10 KVA | 34
equipment distribution transformers 1 phase 15 KVA | 38
equipment distribution transformers 1 phase 25 KVA | 42
equipment distribution transformers 1 phase 37.5 KVA | 48
equipment distribution transformers 1 phase 50 KVA | 51
equipment distribution transformers 1 phase 75 KVA | 57
equipment distribution transformers 1 phase 100 KVA | 66
equipment distribution transformers 1 phase 167 KVA | 75
equipment distribution transformers 3 phase 30 KVA | 50
equipment distribution transformers 3 phase 45 KVA | 54
equipment distribution transformers 3 phase 75 KVA | 66
80 KVA | 70.533
equipment distribution transformers 3 phase 112.5 KVA | 100
equipment distribution transformers 3 phase 150 KVA | 110
equipment distribution transformers 3 phase 225 KVA | 123
equipment distribution transformers 3 phase 300 KVA | 135
400 KVA | 140
equipment distribution transformers 3 phase 500 KVA | 145
equipment generator control panel - 100 AMP | 10
equipment generator control panel - 125 AMP | 10
equipment generator control panel - 150 AMP | 12
equipment generator control panel - 200 AMP | 12
equipment generator control panel - 225 AMP | 15
equipment generator control panel - 250 AMP | 15
equipment generator control panel - 400 AMP | 18
equipment generator control panel - 600 AMP | 22
equipment generator control panel - 800 AMP | 26
equipment generator control panel - 1000 AMP | 30
equipment generator control panel - 1200 AMP | 34
equipment generator control panel - 1400 AMP | 38
equipment generator control panel - 2000 AMP | 44
equipment generator control panel - 2500 AMP | 48
equipment m/a transfer switch - 100 AMP | 10
equipment m/a transfer switch - 125 AMP | 10
equipment m/a transfer switch - 150 AMP | 12
equipment m/a transfer switch - 200 AMP | 12
equipment m/a transfer switch - 225 AMP | 15
equipment m/a transfer switch - 250 AMP | 15
equipment m/a transfer switch - 400 AMP | 18
equipment m/a transfer switch - 600 AMP | 22
equipment m/a transfer switch - 800 AMP | 26
equipment m/a transfer switch - 1000 AMP | 30
equipment m/a transfer switch - 1200 AMP | 34
equipment m/a transfer switch - 1400 AMP | 38
equipment m/a transfer switch - 2000 AMP | 44
equipment m/a transfer switch - 2500 AMP | 48
equipment dc electrical equipment storage baterries STORAGE BATTERIES WITH ACCESSORIES | 2
equipment dc electrical equipment ups,rectifier,inverter UPS RECTIFIER & INVERTER | 30
equipment dc electrical equipment dc panel and charger UPS BATTERY CHARGER | 24
equipment substation, switchyard & transmision lines distribution power transformer 500 KVA | 145
equipment substation, switchyard & transmision lines distribution power transformer 750 KVA | 160
equipment substation, switchyard & transmision lines distribution power transformer 1,000 KVA | 176
equipment substation, switchyard & transmision lines distribution power transformer 1,500 KVA | 224
equipment substation, switchyard & transmision lines distribution power transformer 2,000 KVA | 235
equipment substation, switchyard & transmision lines distribution power transformer 2,500 KVA | 256
equipment substation, switchyard & transmision lines distribution power transformer 3,000 KVA | 280
equipment substation, switchyard & transmision lines distribution power transformer 3,750 KVA | 320
equipment substation, switchyard & transmision lines distribution power transformer 4,000 KVA | 340
equipment substation, switchyard & transmision lines distribution power transformer 5,000 KVA | 420
equipment substation, switchyard & transmision lines distribution power transformer 7,500 KVA | 450
equipment substation, switchyard & transmision lines distribution power transformer 10,000 KVA | 520
equipment substation, switchyard & transmision lines switchyard power transformer 12,000 KVA | 550
equipment substation, switchyard & transmision lines switchyard power transformer 15,000 KVA | 590
equipment substation, switchyard & transmision lines switchyard power transformer 20,000 KVA | 630
equipment substation, switchyard & transmision lines switchyard power transformer 25,000 KVA | 670
equipment substation, switchyard & transmision lines switchyard power transformer 30,000 KVA | 710
equipment substation, switchyard & transmision lines switchyard power transformer 40,000 KVA | 780
50 MVA | 827
100 MVA | 1104
150 MVA | 1476
200 MVA | 1973
225 MVA | 2221.5
275 MVA | 2718.5
300 MVA | 2967
325 MVA | 3215.5
350 MVA | 3464
375 MVA | 3712.5
400 MVA | 3961
equipment substation, switchyard & transmision lines switchyard power transformer DRUM LOADING | 2
equipment substation, switchyard & transmision lines switchyard power transformer TANK CAR LOADING | 0.014
equipment substation, switchyard & transmision lines switchyard power transformer - | -
equipment substation, switchyard & transmision lines substation-structural steel SUBSTATION - STRUCTURAL STEEL | 20
equipment substation, switchyard & transmision lines trap line 400 Amp | 4
equipment substation, switchyard & transmision lines trap line 800 Amp | 6
equipment substation, switchyard & transmision lines trap line 1200 Amp | 8
equipment substation, switchyard & transmision lines trap line 1600 Amp | 14
equipment substation, switchyard & transmision lines trap line 2000 Amp | 22
equipment substation, switchyard & transmision lines trap line 3000 Amp | 25
equipment substation, switchyard & transmision lines hv capacitor-1 phase 50 KAVC | 4
equipment substation, switchyard & transmision lines hv capacitor-1 phase 100 KAVC | 5
equipment substation, switchyard & transmision lines hv capacitor-1 phase 150 KAVC | 6
equipment substation, switchyard & transmision lines hv capacitor-1 phase 200 KAVC | 7
equipment substation, switchyard & transmision lines hv capacitor-3 phase 300 KAVC | 16
equipment substation, switchyard & transmision lines hv capacitor-3 phase 600 KAVC | 17
equipment substation, switchyard & transmision lines hv capacitor-3 phase 900 KAVC | 20
equipment substation, switchyard & transmision lines hv capacitor-3 phase 1,200 KAVC | 24
equipment substation, switchyard & transmision lines hv capacitor-3 phase 1,500 KAVC | 26
equipment substation, switchyard & transmision lines coupling capacitor-potential device 34.5 KV | 22
equipment substation, switchyard & transmision lines coupling capacitor-potential device 46 KV | 25
equipment substation, switchyard & transmision lines coupling capacitor-potential device 69 KV | 26
equipment substation, switchyard & transmision lines coupling capacitor-potential device 115 KV | 28
equipment substation, switchyard & transmision lines coupling capacitor-potential device 138 KV | 29
equipment substation, switchyard & transmision lines coupling capacitor-potential device 161 KV | 30
equipment substation, switchyard & transmision lines coupling capacitor-potential device 230 KV | 32
equipment substation, switchyard & transmision lines coupling capacitor-potential device - | -
equipment substation, switchyard & transmision lines switchyard potential transformer 4 KV, SINGLE PHASE, DRY TYPE | 3
equipment substation, switchyard & transmision lines switchyard potential transformer 7.2 KV, SINGLE PHASE, DRY TYPE | 4
equipment substation, switchyard & transmision lines switchyard potential transformer 14.4 KV, SINGLE PHASE, DRY TYPE | 8
equipment substation, switchyard & transmision lines switchyard potential transformer 23 KV, SINGLE PHASE, DRY TYPE | 9
equipment substation, switchyard & transmision lines switchyard potential transformer 34.5 KV, SINGLE PHASE, DRY TYPE | 10
equipment substation, switchyard & transmision lines switchyard potential transformer 46 KV, SINGLE PHASE, DRY TYPE | 12
equipment substation, switchyard & transmision lines switchyard potential transformer 69 KV, SINGLE PHASE, DRY TYPE | 19
equipment substation, switchyard & transmision lines switchyard potential transformer 115 KV, SINGLE PHASE, OIL TYPE | 25
equipment substation, switchyard & transmision lines switchyard potential transformer 138 KV, SINGLE PHASE, OIL TYPE | 27
equipment substation, switchyard & transmision lines switchyard potential transformer 161 KV, SINGLE PHASE, OIL TYPE | 31
equipment substation, switchyard & transmision lines switchyard potential transformer 230 KV, SINGLE PHASE, OIL TYPE | 32
equipment substation, switchyard & transmision lines switchyard potential transformer 92 KV, THREE PHASE, OIL TYPE | 72
equipment substation, switchyard & transmision lines switchyard potential transformer 115 KV, THREE PHASE, OIL TYPE | 79
equipment substation, switchyard & transmision lines switchyard potential transformer 138 KV, THREE PHASE, OIL TYPE | 86
equipment substation, switchyard & transmision lines switchyard potential transformer 161 KV, THREE PHASE, OIL TYPE | 86
equipment substation, switchyard & transmision lines switchyard potential transformer - | -
equipment substation, switchyard & transmision lines current transformer 5 KV, SINGLE PHASE | 6
equipment substation, switchyard & transmision lines current transformer 7.5 KV, SINGLE PHASE | 6
equipment substation, switchyard & transmision lines current transformer 13.8 KV, SINGLE PHASE | 7
equipment substation, switchyard & transmision lines current transformer 23 KV, SINGLE PHASE | 9
equipment substation, switchyard & transmision lines current transformer 27 KV, SINGLE PHASE | 16
equipment substation, switchyard & transmision lines current transformer 34.5 KV, SINGLE PHASE | 16
equipment substation, switchyard & transmision lines current transformer 46 KV, SINGLE PHASE | 17
equipment substation, switchyard & transmision lines current transformer 69 KV, SINGLE PHASE | 19
equipment substation, switchyard & transmision lines current transformer 115 KV, SINGLE PHASE | 31
equipment substation, switchyard & transmision lines current transformer 138 KV, SINGLE PHASE | 32
equipment substation, switchyard & transmision lines current transformer 161 KV, SINGLE PHASE | 43
equipment substation, switchyard & transmision lines current transformer 234 KV, SINGLE PHASE | 54
equipment substation, switchyard & transmision lines lightning resistor 3 KV, RMS | 2
equipment substation, switchyard & transmision lines lightning resistor 6 KV, RMS | 3
equipment substation, switchyard & transmision lines lightning resistor 9 KV, RMS | 5
equipment substation, switchyard & transmision lines lightning resistor 12 KV, RMS | 6
equipment substation, switchyard & transmision lines lightning resistor 21 KV, RMS | 12
equipment substation, switchyard & transmision lines lightning resistor 37 KV, RMS | 17
equipment substation, switchyard & transmision lines lightning resistor 60 KV, RMS | 19
equipment substation, switchyard & transmision lines lightning resistor 96 KV, RMS | 21
equipment substation, switchyard & transmision lines lightning resistor 108 KV, RMS | 22
equipment substation, switchyard & transmision lines lightning resistor 120 KV, RMS | 23
equipment substation, switchyard & transmision lines lightning resistor 132 KV, RMS | 24
equipment substation, switchyard & transmision lines lightning resistor 144 KV, RMS | 25
equipment substation, switchyard & transmision lines lightning resistor 168 KV, RMS | 27
equipment substation, switchyard & transmision lines lightning resistor 198 KV, RMS | 29
equipment substation, switchyard & transmision lines lightning resistor 228 KV, RMS | 31
equipment substation, switchyard & transmision lines lightning resistor 300 KV, RMS | 35
equipment substation, switchyard & transmision lines lightning resistor - | -
equipment substation, switchyard & transmision lines neutral ground resistor 2.4 KV, 100 - 400 AMP | 31
equipment substation, switchyard & transmision lines neutral ground resistor 2.4 KV, 500 - 1000 AMP | 38
equipment substation, switchyard & transmision lines neutral ground resistor 4 KV, 100 - 400 AMP | 46
equipment substation, switchyard & transmision lines neutral ground resistor 4 KV, 400 - 500 AMP | 54
equipment substation, switchyard & transmision lines neutral ground resistor 8 KV, 100 - 400 AMP | 62
equipment substation, switchyard & transmision lines neutral ground resistor 8 KV, 400 - 500 AMP | 77
equipment substation, switchyard & transmision lines neutral ground resistor 20 KV, 200 - 600 AMP | 92
equipment substation, switchyard & transmision lines disconnect switch 15 KV, 600 AMP | 17
equipment substation, switchyard & transmision lines disconnect switch 15 KV, 1200 AMP | 23
equipment substation, switchyard & transmision lines disconnect switch 15 KV, 2000 AMP | 25
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 600 AMP | 25
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 1200 AMP | 29
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 2000 AMP | 34
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 600 AMP | 29
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 1200 AMP | 33
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 2000 AMP | 36
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 600 AMP | 34
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 1200 AMP | 36
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 2000 AMP | 40
equipment substation, switchyard & transmision lines disconnect switch 115 KV, 600 AMP | 42
equipment substation, switchyard & transmision lines disconnect switch 115 KV, 1200 AMP | 45
equipment substation, switchyard & transmision lines disconnect switch 115 KV, 2000 AMP | 48
equipment substation, switchyard & transmision lines disconnect switch 138 KV, 600 AMP | 54
equipment substation, switchyard & transmision lines disconnect switch 138 KV, 1200 AMP | 57
equipment substation, switchyard & transmision lines disconnect switch 138 KV, 2000 AMP | 63
equipment substation, switchyard & transmision lines disconnect switch 161 KV, 600 AMP | 66
equipment substation, switchyard & transmision lines disconnect switch 161 KV, 1200 AMP | 70
equipment substation, switchyard & transmision lines disconnect switch 161 KV, 2000 AMP | 77
equipment substation, switchyard & transmision lines disconnect switch 230 KV, 600 AMP | 83
equipment substation, switchyard & transmision lines disconnect switch 230 KV, 1200 AMP | 87
equipment substation, switchyard & transmision lines disconnect switch 230 KV, 2000 AMP | 92
equipment substation, switchyard & transmision lines disconnect switch 4 KV, 600 AMP | 3
equipment substation, switchyard & transmision lines disconnect switch 4 KV, 1200 AMP | 3
equipment substation, switchyard & transmision lines disconnect switch 4 KV, 2000 AMP | 3
equipment substation, switchyard & transmision lines disconnect switch 7.2 KV, 600 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 7.2 KV, 1200 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 7.2 KV, 2000 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 14.4 KV, 600 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 14.4 KV, 1200 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 14.4 KV, 2000 AMP | 4
equipment substation, switchyard & transmision lines disconnect switch 23 KV, 600 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 23 KV, 1200 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 23 KV, 2000 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 600 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 1200 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 34.5 KV, 2000 AMP | 5
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 600 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 1200 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch 46 KV, 2000 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 600 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 1200 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch 69 KV, 2000 AMP | 6
equipment substation, switchyard & transmision lines disconnect switch - | -
equipment substation, switchyard & transmision lines oil circuit breaker 14.4 KV, 1200 AMP | 29
equipment substation, switchyard & transmision lines oil circuit breaker 14.4 KV, 3000 AMP | 31
equipment substation, switchyard & transmision lines oil circuit breaker 14.4 KV, 4000 AMP | 35
equipment substation, switchyard & transmision lines oil circuit breaker 23 KV, 1200 AMP | 37
equipment substation, switchyard & transmision lines oil circuit breaker 23 KV, 3000 AMP | 42
equipment substation, switchyard & transmision lines oil circuit breaker 23 KV, 4000 AMP | 48
equipment substation, switchyard & transmision lines oil circuit breaker 34.5 KV, 1200 AMP | 46
equipment substation, switchyard & transmision lines oil circuit breaker 34.5 KV, 3000 AMP | 54
equipment substation, switchyard & transmision lines oil circuit breaker 34.5 KV, 4000 AMP | 62
equipment substation, switchyard & transmision lines oil circuit breaker 46 KV, 1200 AMP | 65
equipment substation, switchyard & transmision lines oil circuit breaker 46 KV, 3000 AMP | 69
equipment substation, switchyard & transmision lines oil circuit breaker 46 KV, 4000 AMP | 73
equipment substation, switchyard & transmision lines oil circuit breaker 69 KV, 1200 AMP | 83
equipment substation, switchyard & transmision lines oil circuit breaker 69 KV, 1600 AMP | 86
equipment substation, switchyard & transmision lines oil circuit breaker 69 KV, 2000 AMP | 116
equipment substation, switchyard & transmision lines oil circuit breaker 115 KV, 1200 AMP | 166
equipment substation, switchyard & transmision lines oil circuit breaker 115 KV, 1600 AMP | 169
equipment substation, switchyard & transmision lines oil circuit breaker 115 KV, 2000 AMP | 181
equipment substation, switchyard & transmision lines oil circuit breaker 115 KV, 3000 AMP | 210
equipment substation, switchyard & transmision lines oil circuit breaker 138 KV, 1200 AMP | 189
equipment substation, switchyard & transmision lines oil circuit breaker 138 KV, 1600 AMP | 196
equipment substation, switchyard & transmision lines oil circuit breaker 138 KV, 2000 AMP | 200
equipment substation, switchyard & transmision lines oil circuit breaker 138 KV, 3000 AMP | 208
equipment substation, switchyard & transmision lines oil circuit breaker 161 KV, 1200 AMP | 212
equipment substation, switchyard & transmision lines oil circuit breaker 161 KV, 1600 AMP | 215
equipment substation, switchyard & transmision lines oil circuit breaker 161 KV, 2000 AMP | 223
equipment substation, switchyard & transmision lines oil circuit breaker 230 KV, 2000 AMP | 231
equipment substation, switchyard & transmision lines load break switch INSTALL LOAD BREAK SWITCHES | 25
equipment substation, switchyard & transmision lines fuse cut out INSTALL FUSE CUT-OUT | 5
equipment substation, switchyard & transmision lines lightning protection INSTALL LIGHTNING PROTECTION SYSTEM | 5
substation, switchyard & transmision lines tubular bus bar,aluminum - 1/2 ", IPS | 0.299
substation, switchyard & transmision lines tubular bus bar,aluminum - 3/4 ", IPS | 0.4
substation, switchyard & transmision lines tubular bus bar,aluminum - 1 ", IPS | 0.465
substation, switchyard & transmision lines tubular bus bar,aluminum - 1 - 1/4 ", IPS | 0.552
substation, switchyard & transmision lines tubular bus bar,aluminum - 1 - 1/2 ", IPS | 0.765
substation, switchyard & transmision lines tubular bus bar,aluminum - 2 ", IPS | 0.797
substation, switchyard & transmision lines tubular bus bar,aluminum - 2 - 1/2 ", IPS | 0.833
substation, switchyard & transmision lines tubular bus bar,aluminum - 3 ", IPS | 1.663
substation, switchyard & transmision lines tubular bus bar,aluminum - 4 ", IPS | 1.999
substation, switchyard & transmision lines tubular bus bar,aluminum - 5 ", IPS | 2.464
substation, switchyard & transmision lines tubular bus bar,aluminum - 6 ", IPS | 3.034
substation, switchyard & transmision lines tubular bus bar,copper - 1/2 ", IPS | 0.4
substation, switchyard & transmision lines tubular bus bar,copper - 3/4 ", IPS | 0.433
substation, switchyard & transmision lines tubular bus bar,copper - 1 ", IPS | 0.498
substation, switchyard & transmision lines tubular bus bar,copper - 1 - 1/4 ", IPS | 0.599
substation, switchyard & transmision lines tubular bus bar,copper - 1 - 1/2 ", IPS | 0.833
substation, switchyard & transmision lines tubular bus bar,copper - 2 ", IPS | 0.866
substation, switchyard & transmision lines tubular bus bar,copper - 2 - 1/2 ", IPS | 0.902
substation, switchyard & transmision lines tubular bus bar,copper - 3 ", IPS | 1.8
substation, switchyard & transmision lines tubular bus bar,copper - 4 ", IPS | 2.165
substation, switchyard & transmision lines tubular bus bar,copper - 5 ", IPS | 2.67
substation, switchyard & transmision lines tubular bus bar,copper - 6 ", IPS | 3.287
substation, switchyard & transmision lines static wire - EXTRA HIGH STRENGTH ( EHS ), 3/8 " | 0.236
substation, switchyard & transmision lines static wire - EXTRA HIGH STRENGTH ( EHS ), 1/2 " | 0.27
substation, switchyard & transmision lines static wire - COPPERWELD ( CWD ), # 6 | 0.179
substation, switchyard & transmision lines static wire - ALUMOWELD, 3 # 7 | 0.189
substation, switchyard & transmision lines acsr - # 6 ( 14.00 sq. mm.) | 0.041
substation, switchyard & transmision lines acsr - # 4 ( 22.00 sq. mm.) | 0.046
substation, switchyard & transmision lines acsr - # 2 ( 30.00 sq. mm.) | 0.052
substation, switchyard & transmision lines acsr - # 1 ( 38.00 sq. mm.) | 0.062
substation, switchyard & transmision lines acsr - # 1/0 ( 50.00 sq. mm.) | 0.067
substation, switchyard & transmision lines acsr - # 2/0 ( 60.00 sq. mm.) | 0.072
substation, switchyard & transmision lines acsr - # 3/0 ( 80.00 sq. mm.) | 0.077
substation, switchyard & transmision lines acsr - # 4/0 (100.00 sq. mm.) | 0.088
substation, switchyard & transmision lines bare copper wire - 186 AMP - # 2 AWG | 0.101
substation, switchyard & transmision lines bare copper wire - 245 AMP - 1/0 AWG | 0.132
substation, switchyard & transmision lines bare copper wire - 283 AMP - 2/0 AWG | 0.145
substation, switchyard & transmision lines bare copper wire - 332 AMP - 3/0 AWG | 0.162
substation, switchyard & transmision lines bare copper wire - 385 AMP - 4/0 AWG | 0.176
substation, switchyard & transmision lines bare copper wire - 430 AMP - 250 MCM | 0.193
substation, switchyard & transmision lines bare copper wire - 524 AMP - 350 MCM | 0.223
substation, switchyard & transmision lines bare copper wire - 663 AMP - 500 MCM | 0.264
substation, switchyard & transmision lines bare copper wire - 860 AMP - 750 MCM | 0.314
substation, switchyard & transmision lines bare copper wire - 1025 AMP - 1000 MCM | 0.338
substation, switchyard & transmision lines bare copper wire - - | -
substation, switchyard & transmision lines bare acsr, single conductor - 140 AMP - 4 - 6/1 | 0.068
substation, switchyard & transmision lines bare acsr, single conductor - 185 AMP - 2 - 6/1 | 0.081
substation, switchyard & transmision lines bare acsr, single conductor - 240 AMP - 1/0 - 6/1 | 0.105
substation, switchyard & transmision lines bare acsr, single conductor - 275 AMP - 2/0 - 6/1 | 0.125
substation, switchyard & transmision lines bare acsr, single conductor - 315 AMP - 3/0 - 6/1 | 0.142
substation, switchyard & transmision lines bare acsr, single conductor - 360 AMP - 4/0 - 6/1 | 0.162
substation, switchyard & transmision lines bare acsr, single conductor - 455 AMP - 266.8 - 26/7 | 0.176
substation, switchyard & transmision lines bare acsr, single conductor - 530 AMP - 336.4 - 26/7 | 0.196
substation, switchyard & transmision lines bare acsr, single conductor - 585 AMP - 397.5 - 26/7 | 0.213
substation, switchyard & transmision lines bare acsr, single conductor - 660 AMP - 477.8 - 26/7 | 0.233
substation, switchyard & transmision lines bare acsr, single conductor - 725 AMP - 556.5 - 26/7 | 0.25
substation, switchyard & transmision lines bare acsr, single conductor - 785 AMP - 636.0 - 26/7 | 0.274
substation, switchyard & transmision lines bare acsr, single conductor - 845 AMP - 715.0 - 26/7 | 0.294
substation, switchyard & transmision lines bare acsr, single conductor - 905 AMP - 795.0 - 26/7 | 0.318
substation, switchyard & transmision lines bare acsr, single conductor - 950 AMP - 874.5 - 54/7 | 0.324
substation, switchyard & transmision lines bare acsr, single conductor - 955 AMP - 900.0 - 54/7 | 0.331
substation, switchyard & transmision lines bare acsr, single conductor - 995 AMP - 954.0 - 54/7 | 0.348
substation, switchyard & transmision lines bare acsr, single conductor - 1025 AMP - 1033.5 - 54/7 | 0.368
substation, switchyard & transmision lines bare acsr, single conductor - 1175 AMP - 1272.0 - 54/7 | 0.429
substation, switchyard & transmision lines bare acsr, single conductor - 1270 AMP - 1431.0 - 54/7 | 0.47
substation, switchyard & transmision lines bare acsr, single conductor - 1360 AMP - 1590.0 - 54/7 | 0.51
substation, switchyard & transmision lines bare acsr, single conductor - 1540 AMP - 2034.0 - 72/7 | 0.541
substation, switchyard & transmision lines bare acsr, single conductor - 1600 AMP - 2167.0 - 72/7 | 0.588
substation, switchyard & transmision lines bare acsr, single conductor - 1670 AMP - 2312.0 - 76/7 | 0.676
substation, switchyard & transmision lines bare acsr, single conductor - 1755 AMP - 2515.0 - 76/7 | 0.743
substation, switchyard & transmision lines insulators suspension type 4 KV, SUSPENSION TYPE | 0.5
substation, switchyard & transmision lines insulators suspension type 7.5 KV, SUSPENSION TYPE | 0.5
substation, switchyard & transmision lines insulators suspension type 13.8 KV, SUSPENSION TYPE | 1
substation, switchyard & transmision lines insulators suspension type 23 KV, SUSPENSION TYPE | 1
substation, switchyard & transmision lines insulators suspension type 27 KV, SUSPENSION TYPE | 1
substation, switchyard & transmision lines insulators suspension type 34.5 KV, SUSPENSION TYPE | 1
substation, switchyard & transmision lines insulators suspension type 66 KV, SUSPENSION TYPE | 1.5
substation, switchyard & transmision lines insulators suspension type 69 KV, SUSPENSION TYPE | 1.5
substation, switchyard & transmision lines insulators suspension type 115 KV, SUSPENSION TYPE | 1.5
substation, switchyard & transmision lines insulators suspension type 138 KV, SUSPENSION TYPE | 2.5
substation, switchyard & transmision lines insulators suspension type 161 KV, SUSPENSION TYPE | 2.5
substation, switchyard & transmision lines insulators suspension type 230 KV, SUSPENSION TYPE | 3
substation, switchyard & transmision lines insulators post type 4 KV, POST TYPE | 0.5
substation, switchyard & transmision lines insulators post type 7.5 KV, POST TYPE | 0.5
substation, switchyard & transmision lines insulators post type 13.8 KV, POST TYPE | 1.3
substation, switchyard & transmision lines insulators post type 23 KV, POST TYPE | 1.4
substation, switchyard & transmision lines insulators post type 27 KV, POST TYPE | 1.4
substation, switchyard & transmision lines insulators post type 34.5 KV, POST TYPE | 3.2
substation, switchyard & transmision lines insulators post type 66 KV, POST TYPE | 4.1
substation, switchyard & transmision lines insulators post type 69 KV, POST TYPE | 4.1
substation, switchyard & transmision lines insulators post type 115 KV, POST TYPE | 4.1
substation, switchyard & transmision lines insulators post type 138 KV, POST TYPE | 5.7
substation, switchyard & transmision lines insulators post type 161 KV, POST TYPE | 5.7
substation, switchyard & transmision lines insulators post type 230 KV, POST TYPE | 6.8
substation, switchyard & transmision lines insulators pin type PIN TYPE | 1.3
substation, switchyard & transmision lines insulators strain type STRAIN TYPE | 1.3
substation, switchyard & transmision lines insulators steel type STEEL TYPE | 2
substation, switchyard & transmision lines insulators suspension type SUSPENSION TYPE | 2.25
substation, switchyard & transmision lines insulators - - | -
poles & hardwares poles and accessories steel galvanized 08 FT. HIGH | 3.2
poles & hardwares poles and accessories steel galvanized 10 FT. HIGH | 4
poles & hardwares poles and accessories steel galvanized 15 FT. HIGH | 5
poles & hardwares poles and accessories steel galvanized 20 FT. HIGH | 5.5
poles & hardwares poles and accessories steel galvanized 30 FT. HIGH | 6
poles & hardwares poles and accessories steel galvanized 33 FT. HIGH | 6.3
poles & hardwares poles and accessories steel galvanized 40 FT. HIGH | 7
poles & hardwares poles and accessories steel galvanized - | -
poles & hardwares poles and accessories pre-cast concrete 10 FT. HIGH | 4.5
poles & hardwares poles and accessories pre-cast concrete 15 FT. HIGH | 5.5
poles & hardwares poles and accessories pre-cast concrete 20 FT. HIGH | 6
poles & hardwares poles and accessories pre-cast concrete 30 FT. HIGH | 6.5
poles & hardwares poles and accessories pre-cast concrete 40 FT. HIGH | 8
poles & hardwares poles and accessories creosoted wood 25 FT. HIGH | 6
poles & hardwares poles and accessories creosoted wood 30 FT. HIGH | 6.5
poles & hardwares poles and accessories creosoted wood 35 FT. HIGH | 7.5
poles & hardwares poles and accessories creosoted wood 40 FT. HIGH | 8.5
poles & hardwares poles and accessories creosoted wood 45 FT. HIGH | 9.5
poles & hardwares poles and accessories creosoted wood 50 FT. HIGH | 10.5
poles & hardwares pole anchor - PLATE ANCHOR | 10
poles & hardwares pole anchor - EXPANSION ANCHOR | 1.3
poles & hardwares pole anchor - SCREW ANCHOR | 2.6
poles & hardwares guys - NO STRAIN INSULATORS | 4.3
poles & hardwares guys - ONE STRAIN INSULATORS | 5.85
poles & hardwares guys - TWO STRAIN INSULATORS | 7.15
poles & hardwares arm guy - NO STRAIN INSULATORS | 4.55
poles & hardwares arm guy - ONE STRAIN INSULATORS | 6.5
poles & hardwares arm guy - TWO STRAIN INSULATORS | 7.8
poles & hardwares down guy - NO STRAIN INSULATORS | 3.9
poles & hardwares down guy - ONE STRAIN INSULATORS | 5.2
poles & hardwares down guy - TWO STRAIN INSULATORS | 6.5
poles & hardwares down guy - - | -
poles & hardwares cross arms - SINGLE ARM | 1.7
poles & hardwares cross arms - DOUBLE ARM | 3.75
poles & hardwares cross arms - SINGLE ARM OR ALLEY ARM | 3.5
poles & hardwares cross arms - DOUBLE ARM OR ALLEY ARM | 5.85
poles & hardwares pins - STEEL SHANK with WASHERS AND NUTS | 0.4
poles & hardwares pins - WOOD SHANK - NAILED | 0.25
poles & hardwares pins - SADDLE PINS | 0.65
poles & hardwares pins - POLE TOP PINS | 1.3
poles & hardwares secondary racks - ONE SPOOL | 0.65
poles & hardwares secondary racks - TWO SPOOL | 1.3
poles & hardwares secondary racks - THREE SPOOL | 1.95
poles & hardwares secondary racks - FOUR SPOOL | 1.95
poles & hardwares secondary racks - RACK EXTENSION | 1.3
cathodic anodes bare graphite 1 " X 60 " | 2.3
cathodic anodes bare graphite 1-1/2 " X 60 " | 2.3
cathodic anodes bare graphite 2 " X 60 " | 3
cathodic anodes bare graphite 2 " X 60 " | 3
cathodic anodes bare graphite 3 " X 30 " | 2.5
cathodic anodes bare graphite 3 " X 60 " | 3.5
cathodic anodes bare graphite 4 " X 40 " | 4
cathodic anodes bare graphite 4 " X 80 " | 5.5
cathodic anodes magnesium 3 " X 3 " X 4.5 " | 0.8
cathodic anodes magnesium 3 " X 3 " X 7.5 " | 0.8
cathodic anodes magnesium 3 " X 3 " X 13.5 " | 1.5
cathodic anodes magnesium 3 " X 3 " X 25.5 " | 2.5
cathodic anodes magnesium 2 " X 2 " X 60.0 " | 3.25
cathodic anodes magnesium 5 " X 5 " X 21.0 " | 4
cathodic anodes magnesium 5 " D X 15 " | 4.75
cathodic anodes zinc 6 " X 56 " , # 8 Wire Size | 4.6
cathodic anodes zinc 6 " X 56 " , # 6 Wire Size | 4.6
cathodic anodes zinc 6 " X 56 " , # 4 Wire Size | 4.6
cathodic anodes zinc 6 " X 56 " , # 2 Wire Size | 4.6
cathodic anodes zinc 6 " X 56 " , # 1 Wire Size | 4.6
cathodic anodes zinc 6 " X 56 " , # 1/0 Wire Size | 5
cathodic anodes zinc 6 " X 56 " , # 2/0 Wire Size | 5
cathodic anodes zinc 6 " X 56 " , # 4/0 Wire Size | 5
cathodic anodes zinc 6 " X 56 " , # 250 Wire Size | 5.4
cathodic anodes zinc 6 " X 56 " , # 300 Wire Size | 5.4
cathodic anodes zinc 6 " X 56 " , # 350 Wire Size | 5.4
cathodic anodes zinc - | -
cathodic air cooled rectifier, pad mounted 12V,1P 4 AMPS | 1.9
cathodic air cooled rectifier, pad mounted 12V,1P 12 AMPS | 1.9
cathodic air cooled rectifier, pad mounted 12V,1P 22 AMPS | 2.3
cathodic air cooled rectifier, pad mounted 12V,1P 50 AMPS | 3.1
cathodic air cooled rectifier, pad mounted 12V,1P 100 AMPS | 6.2
cathodic air cooled rectifier, pad mounted 12V,1P 120 AMPS | 6.9
cathodic air cooled rectifier, pad mounted 24V,1P 4 AMPS | 1.9
cathodic air cooled rectifier, pad mounted 24V,1P 12 AMPS | 2.3
cathodic air cooled rectifier, pad mounted 24V,1P 22 AMPS | 3.1
cathodic air cooled rectifier, pad mounted 24V,1P 50 AMPS | 5.4
cathodic air cooled rectifier, pad mounted 24V,1P 100 AMPS | 7.3
cathodic air cooled rectifier, pad mounted 24V,1P 120 AMPS | 8.1
cathodic air cooled rectifier, pole mounted 12V,1P 4 AMPS | 4.2
cathodic air cooled rectifier, pole mounted 12V,1P 12 AMPS | 4.6
cathodic air cooled rectifier, pole mounted 12V,1P 22 AMPS | 5.4
cathodic air cooled rectifier, pole mounted 12V,1P 50 AMPS | 7.7
cathodic air cooled rectifier, pole mounted 12V,1P 100 AMPS | 14.6
cathodic air cooled rectifier, pole mounted 12V,1P 120 AMPS | 16
cathodic air cooled rectifier, pole mounted 24V,1P 4 AMPS | 4.6
cathodic air cooled rectifier, pole mounted 24V,1P 12 AMPS | 5
cathodic air cooled rectifier, pole mounted 24V,1P 22 AMPS | 6.9
cathodic air cooled rectifier, pole mounted 24V,1P 50 AMPS | 12.3
cathodic air cooled rectifier, pole mounted 24V,1P 100 AMPS | 17.3
cathodic air cooled rectifier, pole mounted 24V,1P 120 AMPS | 21.5
cathodic air cooled rectifier, pad mounted 12V,3P 6 AMPS | 2.7
cathodic air cooled rectifier, pad mounted 12V,3P 12 AMPS | 2.7
cathodic air cooled rectifier, pad mounted 12V,3P 24 AMPS | 3.1
cathodic air cooled rectifier, pad mounted 12V,3P 50 AMPS | 3.8
cathodic air cooled rectifier, pad mounted 12V,3P 100 AMPS | 5
cathodic air cooled rectifier, pad mounted 12V,3P 200 AMPS | 10.8
cathodic air cooled rectifier, pad mounted 24V,3P 6 AMPS | 3.1
cathodic air cooled rectifier, pad mounted 24V,3P 12 AMPS | 3.1
cathodic air cooled rectifier, pad mounted 24V,3P 24 AMPS | 4.2
cathodic air cooled rectifier, pad mounted 24V,3P 50 AMPS | 5.8
cathodic air cooled rectifier, pad mounted 24V,3P 100 AMPS | 7.3
cathodic air cooled rectifier, pad mounted 24V,3P 200 AMPS | 12.3
cathodic air cooled rectifier, pole mounted 12V,3P 6 AMPS | 5.8
cathodic air cooled rectifier, pole mounted 12V,3P 12 AMPS | 6.2
cathodic air cooled rectifier, pole mounted 12V,3P 24 AMPS | 6.9
cathodic air cooled rectifier, pole mounted 12V,3P 50 AMPS | 8.8
cathodic air cooled rectifier, pole mounted 12V,3P 100 AMPS | 11.5
cathodic air cooled rectifier, pole mounted 12V,3P 200 AMPS | 25
cathodic air cooled rectifier, pole mounted 24V,3P 6 AMPS | 6.9
cathodic air cooled rectifier, pole mounted 24V,3P 12 AMPS | 7.3
cathodic air cooled rectifier, pole mounted 24V,3P 24 AMPS | 10.4
cathodic air cooled rectifier, pole mounted 24V,3P 50 AMPS | 13.8
cathodic air cooled rectifier, pole mounted 24V,3P 100 AMPS | 19.2
cathodic air cooled rectifier, pole mounted 24V,3P 200 AMPS | 29.6
cathodic oil emmersed rectifier, pad mounted 12V,1P 4 AMPS | 3.5
cathodic oil emmersed rectifier, pad mounted 12V,1P 12 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 12V,1P 22 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 12V,1P 50 AMPS | 6.5
cathodic oil emmersed rectifier, pad mounted 12V,1P 100 AMPS | 10.5
cathodic oil emmersed rectifier, pad mounted 12V,1P 120 AMPS | 11.5
cathodic oil emmersed rectifier, pad mounted 24V,1P 4 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 24V,1P 12 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,1P 22 AMPS | 5
cathodic oil emmersed rectifier, pad mounted 24V,1P 50 AMPS | 7.7
cathodic oil emmersed rectifier, pad mounted 24V,1P 100 AMPS | 11.2
cathodic oil emmersed rectifier, pad mounted 24V,1P 120 AMPS | 13.5
cathodic oil emmersed rectifier, pole mounted 12V,1P 4 AMPS | 8.5
cathodic oil emmersed rectifier, pole mounted 12V,1P 12 AMPS | 9.2
cathodic oil emmersed rectifier, pole mounted 12V,1P 22 AMPS | 10
cathodic oil emmersed rectifier, pole mounted 12V,1P 50 AMPS | 15.4
cathodic oil emmersed rectifier, pole mounted 12V,1P 100 AMPS | 21.5
cathodic oil emmersed rectifier, pole mounted 12V,1P 120 AMPS | 25
cathodic oil emmersed rectifier, pole mounted 24V,1P 4 AMPS | 9.2
cathodic oil emmersed rectifier, pole mounted 24V,1P 12 AMPS | 9.6
cathodic oil emmersed rectifier, pole mounted 24V,1P 22 AMPS | 11.2
cathodic oil emmersed rectifier, pole mounted 24V,1P 50 AMPS | 18.1
cathodic oil emmersed rectifier, pole mounted 24V,1P 100 AMPS | 25.4
cathodic oil emmersed rectifier, pole mounted 24V,1P 120 AMPS | 28.8
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 4 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 12 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 22 AMPS | 4.6
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 50 AMPS | 6.9
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 100 AMPS | 10.5
cathodic oil emmersed rectifier, pad mounted 12V,1P, explosion proof 120 AMPS | 12.3
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 4 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 12 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 22 AMPS | 5
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 50 AMPS | 8.1
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 100 AMPS | 11.9
cathodic oil emmersed rectifier, pad mounted 24V,1P, explosion proof 120 AMPS | 13.8
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 4 AMPS | 8.8
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 12 AMPS | 9.6
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 22 AMPS | 10.5
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 50 AMPS | 15.8
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 100 AMPS | 22.3
cathodic oil emmersed rectifier, pole mounted 12V,1P, explosion proof 120 AMPS | 26.1
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 4 AMPS | 9.6
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 12 AMPS | 10
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 22 AMPS | 11.9
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 50 AMPS | 18.5
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 100 AMPS | 26.1
cathodic oil emmersed rectifier, pole mounted 24V,1P, explosion proof 120 AMPS | 30.8
cathodic oil emmersed rectifier, pad mounted 12V,3P 6 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 12V,3P 12 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 12V,3P 24 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 12V,3P 50 AMPS | 6.5
cathodic oil emmersed rectifier, pad mounted 12V,3P 100 AMPS | 10.5
cathodic oil emmersed rectifier, pad mounted 12V,3P 200 AMPS | 15
cathodic oil emmersed rectifier, pad mounted 24V,3P 6 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,3P 12 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,3P 24 AMPS | 5
cathodic oil emmersed rectifier, pad mounted 24V,3P 50 AMPS | 7.7
cathodic oil emmersed rectifier, pad mounted 24V,3P 100 AMPS | 11.2
cathodic oil emmersed rectifier, pad mounted 24V,3P 200 AMPS | 16.9
cathodic oil emmersed rectifier, pole mounted 12V,3P 6 AMPS | 8.8
cathodic oil emmersed rectifier, pole mounted 12V,3P 12 AMPS | 9.2
cathodic oil emmersed rectifier, pole mounted 12V,3P 24 AMPS | 10
cathodic oil emmersed rectifier, pole mounted 12V,3P 50 AMPS | 15.4
cathodic oil emmersed rectifier, pole mounted 12V,3P 100 AMPS | 21.9
cathodic oil emmersed rectifier, pole mounted 12V,3P 200 AMPS | 35.8
cathodic oil emmersed rectifier, pole mounted 24V,3P 6 AMPS | 9.6
cathodic oil emmersed rectifier, pole mounted 24V,3P 12 AMPS | 10
cathodic oil emmersed rectifier, pole mounted 24V,3P 24 AMPS | 11.9
cathodic oil emmersed rectifier, pole mounted 24V,3P 50 AMPS | 18.1
cathodic oil emmersed rectifier, pole mounted 24V,3P 100 AMPS | 25.8
cathodic oil emmersed rectifier, pole mounted 24V,3P 200 AMPS | 40.4
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 6 AMPS | 3.8
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 12 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 24 AMPS | 4.6
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 50 AMPS | 6.5
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 100 AMPS | 10.5
cathodic oil emmersed rectifier, pad mounted 12V,3P, explosion proof 200 AMPS | 15.8
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 6 AMPS | 4.2
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 12 AMPS | 4.6
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 24 AMPS | 5.4
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 50 AMPS | 7.7
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 100 AMPS | 11.2
cathodic oil emmersed rectifier, pad mounted 24V,3P, explosion proof 200 AMPS | 17.7
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 6 AMPS | 9.2
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 12 AMPS | 9.6
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 24 AMPS | 10.4
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 50 AMPS | 15.4
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 100 AMPS | 22.7
cathodic oil emmersed rectifier, pole mounted 12V,3P, explosion proof 200 AMPS | 37.3
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 6 AMPS | 10
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 12 AMPS | 10.4
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 24 AMPS | 12.3
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 50 AMPS | 18.1
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 100 AMPS | 26.5
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof 200 AMPS | 42.3
cathodic oil emmersed rectifier, pole mounted 24V,3P, explosion proof - | -
cathodic cathodic cable - 1/C # 8 | 0.036
cathodic cathodic cable - 1/C # 6 | 0.043
cathodic cathodic cable - 1/C # 4 | 0.049
cathodic cathodic cable - 1/C # 2 | 0.059
cathodic cathodic cable - 1/C # 1 | 0.066
cathodic cathodic cable - 1/C # 1/0 | 0.072
cathodic cathodic cable - 1/C # 2/0 | 0.082
cathodic cathodic cable - 1/C # 4/0 | 0.098
cathodic cathodic cable - 1/C # 250 | 0.112
cathodic cathodic cable - 1/C # 300 | 0.121
cathodic cathodic cable - 1/C # 350 | 0.128
heat tracing heater strip - HEATER STRIP | 0.05
heat tracing polymatrix Dual Power Connection Kit (w/ Junction Box) Dual Power Connection Kit (w/ Junction Box) | 2.1
heat tracing polymatrix Single Power Connection Kit (w/ Junction Box) Single Power Connection Kit (w/ Junction Box) | 1.1
heat tracing polymatrix Power Connection Kit Power Connection Kit | 1
heat tracing polymatrix Splice Kit Splice Kit | 1.5
heat tracing polymatrix Tee Kit Tee Kit | 2
heat tracing polymatrix End Seal Kit End Seal Kit | 0.2
heat tracing automatrix Power Connection Kit (w/ Junction Box) Power Connection Kit (w/ Junction Box) | 1
heat tracing automatrix Splice Kit (w/ Junction Box) Splice Kit (w/ Junction Box) | 1.5
heat tracing automatrix Tee Kit (w/ Junction Box) Tee Kit (w/ Junction Box) | 2
heat tracing automatrix End Seal Kit End Seal Kit | 0.2
instrument alarm - INSTRUMENT TYPE - ALARMS | Install
instrument alarm analyzer ANALYZER ALARM - HIGH AND LOW | 1.4
instrument alarm burner BURNER ALARM - HIGH AND LOW | 1.4
instrument alarm flow FLOW ALARM | 1.4
instrument alarm flow FLOW ALARM - HIGH | 1.4
instrument alarm flow FLOW ALARM - HIGH / LOW | 1.4
instrument alarm flow FLOW ALARM - LOW | 1.4
instrument alarm flow FLOW ALARM - LOW / HIGH | 1
instrument alarm flow FLOW ALARM - LOW / LOW | 1
instrument alarm level LEVEL ALARM | 1.4
instrument alarm level LEVEL ALARM - HIGH | 1.4
instrument alarm level LEVEL ALARM - HIGH HIGH | 1
instrument alarm level LEVEL ALARM - HIGH / LOW | 1.4
instrument alarm level LEVEL ALARM - LOW | 1.4
instrument alarm level LEVEL ALARM - LOW / HIGH | 1
instrument alarm level LEVEL ALARM - LOW LOW | 1
instrument alarm pressure PRESURRE ALARM - | 1.4
instrument alarm pressure PRESURRE ALARM - HIGH | 1.4
instrument alarm pressure PRESURRE ALARM - HIGH HIGH | 1
instrument alarm pressure PRESURRE ALARM - HIGH / LOW | 1.4
instrument alarm pressure PRESURRE ALARM - LOW | 1.4
instrument alarm pressure PRESURRE ALARM - LOW / HIGH | 1
instrument alarm pressure PRESURRE ALARM - LOW LOW | 1
instrument alarm pressure PRESURRE DIFF. ALARM HIGH | 1
instrument alarm pressure PRESURRE DIFF. ALARM HIGH HIGH | 1
instrument alarm temperature TEMPERATURE ALARM | 1.4
instrument alarm temperature TEMPERATURE ALARM - HIGH | 1.4
instrument alarm temperature TEMPERATURE ALARM - HIGH HIGH | 1
instrument alarm temperature TEMPERATURE ALARM - HIGH / LOW | 1.4
instrument alarm temperature TEMPERATURE ALARM - LOW | 1.4
instrument alarm temperature TEMPERATURE ALARM - LOW / HIGH | 1
instrument alarm alarm ALARM | 2
instrument alarm - - | -
instrument control valves - INSTRUMENT TYPE - CONTROL VALVES | Install
instrument control valves analyzer ANALYZER VALVE | 0
instrument control valves control CONTROL VALVE | 0
instrument control valves flow FLOW CONTROL VALVE | 0
instrument control valves flow FLOW VALVE | 0
instrument control valves hand HAND CONTROL VALVE | 0
instrument control valves hand HAND VALVE | 0
instrument control valves level LEVEL CONTROL VALVE | 0
instrument control valves level LEVEL VALVE | 0
instrument control valves pressure PRESSURE CONTROL VALVE | 0
instrument control valves pressure PRESSURE VALVE | 0
instrument control valves temperature TEMPERATURE CONTROL VALVE | 0
instrument control valves temperature TEMPERATURE VALVE | 0
instrument control valves temperature CONTROL VALVE | 0
instrument control valves - - | -
instrument controllers - INSTRUMENT TYPE - CONTROLLERS | Install
instrument controllers analyzer ANALYZER CONTROLLER | 8
instrument controllers flow FLOW CONTROLLER | 8
instrument controllers hand HAND CONTROLLER ( MANUAL ) | 2
instrument controllers hand HAND INDICATING CONTROLLER (MANUAL) | 2
instrument controllers time TIME CONTROLLER ( MANUAL ) | 8
instrument controllers level LEVEL CONTROLLER | 8
instrument controllers pressure PRESSURE CONTROLLER | 8
instrument controllers temperature TEMPERATURE CONTROLLER | 8
instrument controllers weight WEIGHT CONTROLLER | 8
instrument elements - INSTRUMENT TYPE - ELEMENTS | Install
instrument elements analyzer ANALYZER ELEMENT | 1
instrument elements burner BURNER ELEMENT | 2.5
instrument elements conductivity CONDUCTIVITY ELEMENT | 4
instrument elements density DENSITY ELEMENT | 8
instrument elements flow FLOW ELEMENT ( ORIFICE PLATE ) | 1
instrument elements orifice ORIFICE PLATE | 1
instrument elements current CURRENT ELEMENT | 4
instrument elements level LEVEL ELEMENT | 6
instrument elements moisture MOISTURE ELEMENT | 4
instrument elements pressure PRESSURE ELEMENT | 2
instrument elements restriction RESTRICTION ORIFICE | 1
instrument elements speed SPEED ELEMENT | 4
instrument elements temperature TEMPERATURE ELEMENT | 2
instrument elements viscosity VISCOSITY ELEMENT | 2.5
instrument elements weight WEIGHT ELEMENT | 16
instrument elements - - | -
instrument indicator - INSTRUMENT TYPE - INDICATORS | Install
instrument indicator analyzer ANALYZER INDICATOR | 6
instrument indicator analyzer ANALYZER INDICATING CONTROLLER | 8
instrument indicator flow FLOW INDICATOR ( PNEU. TYPE ) | 2
instrument indicator flow FLOW INDICATING CONTROLLER | 8
instrument indicator current CURRENT INDICATOR | 6
instrument indicator electronic ELECTRONIC TIMER | 4
instrument indicator level LEVEL INDICATOR | 3
instrument indicator level LEVEL INDICATING CONTROLLER | 10
instrument indicator pressure PRESSURE DIFFERENTIAL INDICATOR | 6
instrument indicator pressure PRESSURE DIFF. INDIC. CONTROLLER | 8
instrument indicator pressure PRESSURE INDICATOR | 2
instrument indicator pressure PRESSURE INDICATING CONTROLLER | 8
instrument indicator temperature TEMPERATURE INDICATOR | 2
instrument indicator temperature TEMPERATURE INDICATING CONTROLLER | 8
instrument indicator weight WEIGHT INDICATOR | 8
instrument indicator weight WEIGHT INDICATING CONTROLLER | 8
instrument indicator position POSITION INDICATOR | 2
instrument indicator - - | -
instrument recorder - INSTRUMENT TYPE - RECORDERS | Install
instrument recorder analyzer ANALYZER RECORDER | 8
instrument recorder flow FLOW RECORDER | 8
instrument recorder flow FLOW RECORDER CONTROLLER | 9
instrument recorder level LEVEL RECORDER | 8
instrument recorder pressure PRESSURE RECORDER | 8
instrument recorder pressure PRESSURE RECORDING CONTROLLER | 8
instrument recorder temperature TEMPERATURE RECORDER | 8
instrument recorder temperature TEMPERATURE RECORDER CONTROLLER | 8
instrument recorder weight WEIGHT RECORDER | 8
instrument recorder - - | -
instrument switch - INSTRUMENT TYPE - SWITCHES | Install
instrument switch analyzer ANALYZER SWITCH HIGH | 3
instrument switch analyzer ANALYZER SWITCH LOW | 3
instrument switch burner BURNER SWITCH | 3
instrument switch burner BURNER SWITCH HIGH | 3
instrument switch burner BURNER SWITCH LOW | 3
instrument switch flow FLOW INDICATING SWITCH | 7
instrument switch flow FLOW INDICATING SWITCH HIGH | 7
instrument switch flow FLOW INDICATING SWITCH HIGH / LOW | 7
instrument switch flow FLOW INDICATING SWITCH LOW | 7
instrument switch flow FLOW INDICATING SWITCH LOW / HIGH | 7
instrument switch flow FLOW SWITCH | 7
instrument switch flow FLOW SWITCH HIGH | 7
instrument switch flow FLOW SWITCH HIGH / LOW | 7
instrument switch flow FLOW SWITCH LOW | 7
instrument switch flow FLOW SWITCH LOW / HIGH | 7
instrument switch flow FLOW SWITCH LOW / LOW | 7
instrument switch hand HAND SWITCH | 2
instrument switch current CURRENT SWITCH | 4
instrument switch timer TIMER SWITCH | 4
instrument switch level LEVEL SWITCH | 10
instrument switch level LEVEL SWITCH HIGH | 10
instrument switch level LEVEL SWITCH HIGH HIGH | 10
instrument switch level LEVEL SWITCH HIGH / LOW | 10
instrument switch level LEVEL SWITCH LOW | 10
instrument switch level LEVEL SWITCH LOW / HIGH | 10
instrument switch level LEVEL SWITCH LOW LOW | 10
instrument switch pressure PRESSURE DIFF. INDIC. SWITCH | 6
instrument switch pressure PRESSURE DIFF. INDIC. SWITCH High | 6
instrument switch pressure PRESSURE DIFF. INDIC. SWITCH High/Low | 6
instrument switch pressure PRESSURE DIFF. INDIC. SWITCH Low | 6
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH | 4
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH High | 4
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH High/High | 2
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH High/Low | 4
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH Low | 4
instrument switch pressure PRESSURE DIFFERENTIAL SWITCH Low/High | 2
instrument switch pressure PRESSURE SWITCH | 4
instrument switch pressure PRESSURE SAFETY ELEMENT | 0.5
instrument switch pressure PRESSURE SWITCH HIGH | 4
instrument switch pressure PRESSURE SWITCH HIGH HIGH | 2
instrument switch pressure PRESSURE SWITCH HIGH / LOW | 4
instrument switch pressure PRESSURE SWITCH LOW | 4
instrument switch pressure PRESSURE SWITCH LOW / HIGH | 2
instrument switch pressure PRESSURE SWITCH LOW LOW | 2
instrument switch pressure PRESSURE SAFETY VALVE | 0
instrument switch speed switch SPEED SWITCH | 2
instrument switch speed switch SPEED SWITCH HIGH | 2
instrument switch speed switch SPEED SWITCH LOW | 2
instrument switch temperature TEMPERATURE SWITCH | 2
instrument switch temperature TEMPERATURE SWITCH HIGH | 2
instrument switch temperature TEMPERATURE SWITCH LOW | 2
instrument switch temperature TEMPERATURE SWITCH HIGH LOW | 2
instrument switch limit LIMIT SWITCH | 1
instrument switch limit LIMIT SWITCH HIGH | 1
instrument switch limit LIMIT SWITCH LOW | 1
instrument switch temperature TEMPERATURE INDICATING SWITCH | 2
instrument switch temperature TEMPERATURE INDICATING SWITCH High | 2
instrument switch temperature TEMPERATURE INDICATING SWITCH Low | 2
instrument switch temperature TEMPERATURE INDICATING SWITCH H/L | 2
instrument switch limit/proximity LIMIT / PROXIMITY SWITCH | 1
instrument switch limit/proximity LIMIT / PROXIMITY SWITCH HIGH | 1
instrument switch limit/proximity LIMIT / PROXIMITY SWITCH LOW | 1
instrument switch - - | -
instrument pressure - INSTRUMENT TYPE - PRESSURE ITEMS | Install
instrument pressure pressure PRESSURE SAFETY ELEMENT | 1
instrument pressure rupture RUPTURE DISK | 1
instrument pressure pressure PRESSURE SAFETY VALVE | 0
instrument pressure reliefe RELIEF VALVE | 0
instrument solenoid valves - INSTRUMENT TYPE - SOLENOID VALVES | Install
instrument solenoid valves flow FLOW SOLENOID | 2
instrument solenoid valves level LEVEL SOLENOID | 2
instrument solenoid valves pressure PRESSURE SOLENOID | 2
instrument solenoid valves temperature TEMPERATURE SOLENOID | 2
instrument solenoid valves solenoid SOLENOID VALVE | 2
instrument solenoid valves - - | -
instrument transmitter - INSTRUMENT TYPE - TRANSMITTERS | Install
instrument transmitter analyzer ANALYZER TRANSMITTER | 4
instrument transmitter analyzer ANALYZER INDICATING TRANSMITTER | 4
instrument transmitter density DENSITY TRANSMITTER | 8
instrument transmitter flow FLOW TRANSMITTER | 2
instrument transmitter flow FLOW INDICATING TRANSMITTER | 4
instrument transmitter current CURRENT TRANSMITTER | 8
instrument transmitter level LEVEL TRANSMITTER | 8
instrument transmitter level LEVEL INDICATING TRANSMITTER | 8
instrument transmitter moisture MOISTURE TRANSMITTER | 8
instrument transmitter moisture MOISTURE INDICATING TRANSMITTER | 8
instrument transmitter pressure PRESSURE TRANSMITTER | 4
instrument transmitter pressure PRESSURE INDICATING TRANSMITTER | 4
instrument transmitter pressure PRESSURE DIFF. INDICATING TRANSMITTER | 4
instrument transmitter pressure PRESSURE DIFFERENTIAL TRANSMITTER | 4
instrument transmitter temperature TEMPERATURE TRANSMITTER | 4
instrument transmitter temperature TEMPERATURE INDICATING TRANSMITTER | 4
instrument transmitter temperature TEMPERATURE DIFFERENTIAL TRANSMITTER | 2
instrument transmitter viscosity VISCOSITY TRANSMITTER | 8
instrument transmitter weight WEIGHT TRANSMITTER | 8
instrument transmitter weight WEIGHT INDICATING TRANSMITTER | 8
instrument transmitter - - | -
instrument I/P transducer - INSTRUMENT TYPE - I / P TRANSDUCERS | Install
instrument I/P transducer flow FLOW I / P TRANSDUCER | 4
instrument I/P transducer level LEVEL I / P TRANSDUCER | 4
instrument I/P transducer pressure PRESSURE I / P TRANSDUCER | 4
instrument I/P transducer temperature TEMPERATURE I / P TRANSDUCER | 4
instrument I/P transducer - - | -
instrument misc. instrument - INSTRUMENT TYPE - MISC. INSTRUMENTS | Install
instrument misc. instrument flow FLOW TOTALIZER | 8
instrument misc. instrument flow FLOW GLASS | 4
instrument misc. instrument level LEVEL GAUGE W/O BRIDLE | 6
instrument misc. instrument level LEVEL GAUGE W/ BRIDLE | 32
instrument misc. instrument sight SIGHT GLASS | 4
instrument misc. instrument - - | -
instrument panel mounted - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Install
instrument panel mounted - LEVEL ALARM HIGH | 0.5
instrument panel mounted - PRESSURE ALARM LOW | 0.5
instrument panel mounted - TEMPERATURE ALARM HIGH | 0.5
instrument panel mounted - TEMPERATURE ALARM LOW | 0.5
instrument panel mounted - UNCLASSIFIED ALARM | 0.5
instrument panel mounted - FLOW INDICATOR CONTROLLER | 7.4
instrument panel mounted - HAND INDICATOR CONTROLLER | 1.4
instrument panel mounted - PRESSURE INDICATOR CONTROLLER | 4
instrument panel mounted - LEVEL INDICATOR | 2.4
instrument panel mounted - PRESSURE SWITCH LOW | 1
instrument panel mounted - TEMPERATURE SWITCH HIGH | 1
instrument panel mounted - TEMPERATURE SWITCH LOW | 1
instrument panel mounted - UNCLASSIFIED SPEED SWITCH | 1
instrument panel mounted - AIR SWITCH | 1
instrument panel mounted - ANNUNCIATOR POINT, PILOT LIGHT, ALARM | 0.5
instrument panel mounted - AUTO / MANUAL SWITCHING STATION | 2
instrument panel mounted - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Install
instrument panel mounted - CONVERTER, AMPLIFIER, ETC. | 1
instrument panel mounted - ELECTRICAL RELAY, SWITCH, ETC. | 0.5
instrument panel mounted - EQUIPMENT RACKS OR LOCAL PANEL | 24
instrument panel mounted - INDICATING CONTROL STATION | 3
instrument panel mounted - INDICATOR | 1.5
instrument panel mounted - INTEGRATOR | 1.5
instrument panel mounted - MANUAL LOADING STATION | 2
instrument panel mounted - MINIATURE RECORDER | 2
instrument panel mounted - MINIATURE RECORDING CONTROLLER | 4
instrument panel mounted - MULTI - POINT INDICATOR | 12
instrument panel mounted - MULTI - POINT RECORDER | 18
instrument panel mounted - PANEL METER | 1
instrument panel mounted - PANELBOARD OR CONSOLE ( MAIN CTL RM ) | 7
instrument panel mounted - PNEUMATIC COMPUTING RELAYS | 1.5
instrument panel mounted - POWER SUPPLY | 2
instrument panel mounted - PRESSURE SWITCH | 1
instrument panel mounted - PUSHBUTTON OR SELECTOR SWITCH | 0.5
instrument panel mounted - RATIO STATION | 3
instrument panel mounted - RECEIVER GAUGE | 1
instrument panel mounted - RECORDER, LARGE CASE | 3
instrument panel mounted - RECORDING CONTROLLER, LARGE CASE | 6
instrument panel mounted - S.A.V. | 1
instrument panel mounted - - | -
instrument panel mounted - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Install
instrument panel mounted - ONE POINT | 4
instrument panel mounted - TWO POINT | 5
instrument panel mounted - ONE PEN | 4
instrument panel mounted - TWO PEN | 5
instrument panel mounted - THREE PEN | 6
instrument panel mounted - ONE PEN | 5
instrument panel mounted - TWO PEN | 6
instrument panel mounted - THREE PEN | 7
instrument panel mounted - MULTIPOINT TEMPERATURE INDICATOR | 8
instrument panel mounted - MULTIPOINT TEMPERATURE RECORDER | 7
instrument panel mounted - DRAFT GAUGE ONE POINT | 6
instrument panel mounted - ANNUNCIATOR SYSTEM | 15
instrument panel mounted - INTEGRATOR | 5
instrument panel mounted - VOLTAGE OR AMMETER | 3
instrument panel mounted - PUSHBUTTONS | 2
instrument panel mounted - LIGHTS | 2
instrument panel mounted - SELECTOR SWITCHES ( ELECT ) | 2
instrument panel mounted - SELECTOR SWITCHES ( PNEU ) 3 - WAY | 4
instrument panel mounted - SELECTOR SWITCHES ( PNEU ) 4 - WAY | 6
instrument panel mounted - FUNCTION GENERATOR | 7
instrument panel mounted - TRANSDUCERS | 7
instrument panel mounted - CIRCUIT BREAKERS | 1
instrument panel mounted - TERMINAL BOX | 2
instrument panel mounted - DISTRIBUTION PANEL | 10
instrument panel mounted - ( CONT'N. ) | Install
instrument panel mounted - LIMIT HIGH | 5
instrument panel mounted - LIMIT LOW | 5
instrument panel mounted - SELECTOR, HIGH OR LOW | 5
instrument panel mounted - BOOSTER | 5
instrument panel mounted - REVERSING | 5
instrument panel mounted - SWITCHES ( RECEIVER TYPE ) SINGLE | 5
instrument panel mounted - SWITCHES ( RECEIVER TYPE ) DUAL | 6
instrument panel mounted - POWER SUPPLY | 6
instrument panel mounted - CLOCK | 4
instrument panel mounted - AMPLIFIER | 4
instrument panel mounted - ALARM HORN | 4
instrument panel mounted - ALARM MODULE PER POINT | 1
instrument panel mounted - SOLENOID - 2 WAY | 4
instrument panel mounted - SOLENOID - 3 WAY | 4
instrument panel mounted - SOLENOID - 4 WAY | 5
instrument panel mounted - - | -
instrument mounting brackets, stands - MOUNTING BRACKET, STANDS, & w/P HOUSING | FAB/Install
instrument mounting brackets, stands - WALL OR SURFACE BRACKET | 2.0 / 3.0
instrument mounting brackets, stands - FLOOR STAND - SMALL OR MEDIUM DEVICE | 4.0 / 5.0
instrument mounting brackets, stands - FLOOR STAND - LARGE DEVICE | 8.0 / 8.0
instrument mounting brackets, stands - - VIPAK W/ INTEGRAL HEATING UNIT | 0 / 8.0
instrument mounting brackets, stands - - FLEXPAK | 0 / 2.0
instrument mounting brackets, stands - - | -
instrument connection to process - CONNECTIONS TO PROCESS | INSTALL
instrument connection to process - FLOW OR LEVEL (1) STANDARD | 24
instrument connection to process - (2) WITH SEAL POT | 32
instrument connection to process - (1) STANDARD | 16
instrument connection to process - (2) WITH SEAL POT | 20
instrument connection to process - (1) STANDARD | 2
instrument connection to process - (2) WITH SEAL POT | 3
instrument connection to process - REPLACEMENT LEVEL INSTRUMENT | 10
instrument connection to process - CAPILLARY TUBES | 2
instrument connection to process - - | -
instrument pneumatics air connection PNEUMATICS | INSTALL
instrument pneumatics air connection - AIR SUPPLY FROM INSTRUMENT AIR HEADER | 12
instrument pneumatics air connection - AIR SUPPLY OR PURGE GAS FROM HEADER | 12
instrument pneumatics signal connection - LOCAL SINGLE LINE INCLUDING TUBING | 8
instrument pneumatics tube bundles 7 TUBE | 0.984
instrument pneumatics tube bundles 12 TUBE | 1.312
instrument pneumatics tube bundles 19 TUBE | 1.64
instrument tubing raceway - - TUBING RACEWAYS | INSTALL
instrument tubing raceway - 1" - 3 3/8 " TUBE | 1.968
instrument tubing raceway - 6" - 9 " TUBE | 3.28
instrument tubing raceway - 12" OR LARGER | 3.936
instrument junction box - 7 TUBE | 8
instrument junction box - 12 TUBE | 10
instrument junction box - 19 TUBE | 14
instrument tubing w/ fitting and support - 1/8 " O.D. | 0.689
instrument tubing w/ fitting and support - 1/4 " O.D. | 0.754
instrument tubing w/ fitting and support - 3/8 " O.D. | 0.82
instrument tubing w/ fitting and support - 1/2 " O.D. | 0.918
instrument tubing w/ fitting and support - 5/8 " O.D. | 1.05
instrument tubing w/ fitting and support - 3/4 " O.D. | 1.148
instrument tubing w/ fitting and support - 1 " O.D. | 1.312
1 -1/4" O.D. | 1.476
1 -1/2" O.D. | 1.64
2" O.D. | 1.968
instrument air supply blowdown and test - AIR SUPPLY BLOWDOWN AND TEST | 2
instrument air supply blowdown and test - SIGNAL TEST ( PNEUM. OR ELECT.) | 1
instrument air supply blowdown and test - - | -
instrument tubing, stainless steel - TUBINGS, STAINLESS STEEL | INSTALL
instrument tubing, stainless steel - 3/8 " O.D. TUBE .035" WALL, 316/304 S/S | 0.394
instrument tubing, stainless steel - 1/2 " O.D. TUBE .035" WALL, 316/304 S/S | 0.492
instrument tubing, stainless steel - 5/8 " O.D. TUBE .035" WALL, 316/304 S/S | 0.492
instrument tubing, stainless steel - 3/4 " O.D. TUBE .049" WALL, 316/304 S/S | 0.656
instrument tubing, stainless steel - 1 " O.D. TUBE .065" WALL, 316/304 S/S | 0.82
instrument tubing, stainless steel - 1- 1/4 " O.D. TUBE .083" WALL, 316/304 S/S | 0.918
instrument tubing, stainless steel - 1- 1/2 " O.D. TUBE .095" WALL, 316/304 S/S | 1.082
instrument tubing, stainless steel - 2 " O.D. TUBE .109" WALL, 316/304 S/S | 1.246
instrument tubing, stainless steel - - | -
instrument tube fitting - TUBE FITTINGS | INSTALL
instrument tube fitting elbow, union 3/8 " O.D. , 45/90 DEG ELBOW, UNION | 0.25
instrument tube fitting elbow, union 1/2 " O.D. , 45/90 DEG ELBOW, UNION | 0.45
instrument tube fitting elbow, union 5/8 " O.D. , 45/90 DEG ELBOW, UNION | 0.45
instrument tube fitting elbow, union 3/4 " O.D. , 45/90 DEG ELBOW, UNION | 0.65
instrument tube fitting elbow, union 1 " O.D. , 45/90 DEG ELBOW, UNION | 0.8
instrument tube fitting elbow, union 1- 1/4 " O.D. , 45/90 DEG ELBOW, UNION | 0.9
instrument tube fitting elbow, union 1- 1/2 " O.D. , 45/90 DEG ELBOW, UNION | 1
instrument tube fitting elbow, union 2 " O.D. , 45/90 DEG ELBOW, UNION | 1.1
instrument tube fitting tee, union 3/8 " O.D. , TEE, UNION | 0.35
instrument tube fitting tee, union 1/2 " O.D. , TEE, UNION | 0.65
instrument tube fitting tee, union 5/8 " O.D. , TEE, UNION | 0.65
instrument tube fitting tee, union 3/4 " O.D. , TEE, UNION | 0.85
instrument tube fitting tee, union 1 " O.D. , TEE, UNION | 1
instrument tube fitting tee, union 1- 1/4 " O.D. , TEE, UNION | 1.25
instrument tube fitting tee, union 1- 1/2 " O.D. , TEE, UNION | 1.4
instrument tube fitting tee, union 2 " O.D. , TEE, UNION | 1.5
instrument tube fitting union 3/8 " O.D. , UNION | 0.25
instrument tube fitting union 1/2 " O.D. , UNION | 0.4
instrument tube fitting union 5/8 " O.D. , UNION | 0.6
instrument tube fitting union 3/4 " O.D. , UNION | 0.6
instrument tube fitting union 1 " O.D. , UNION | 0.8
instrument tube fitting union 1- 1/4 " O.D. , UNION | 0.9
instrument tube fitting union 1- 1/2 " O.D. , UNION | 1
instrument tube fitting union 2 " O.D. , UNION | 1.1
instrument tube fitting - TUBE FITTINGS ( CONT'N. ) | INSTALL
instrument tube fitting cap 3/8 " O.D. , CAP | 0.15
instrument tube fitting cap 1/2 " O.D. , CAP | 0.2
instrument tube fitting cap 5/8 " O.D. , CAP | 0.3
instrument tube fitting cap 3/4 " O.D. , CAP | 0.35
instrument tube fitting cap 1 " O.D. , CAP | 0.35
instrument tube fitting cap 1- 1/4 " O.D. , CAP | 0.45
instrument tube fitting cap 1- 1/2 " O.D. , CAP | 0.5
instrument tube fitting cap 2 " O.D. , CAP | 0.55
instrument tube fitting male connector 3/8 " O.D. , MALE CONNECTOR | 0.15
instrument tube fitting male connector 1/2 " O.D. , MALE CONNECTOR | 0.2
instrument tube fitting male connector 5/8 " O.D. , MALE CONNECTOR | 0.25
instrument tube fitting male connector 3/4 " O.D. , MALE CONNECTOR | 0.35
instrument tube fitting male connector 1 " O.D. , MALE CONNECTOR | 0.45
instrument tube fitting male connector 1- 1/4 " O.D. , MALE CONNECTOR | 0.55
instrument tube fitting male connector 1- 1/2 " O.D. , MALE CONNECTOR | 0.6
instrument tube fitting male connector 2 " O.D. , MALE CONNECTOR | 0.65
instrument tube fitting female connector 3/8 " O.D. , FEMALE CONNECTOR | 0.3
instrument tube fitting female connector 1/2 " O.D. , FEMALE CONNECTOR | 0.4
instrument tube fitting female connector 5/8 " O.D. , FEMALE CONNECTOR | 0.55
instrument tube fitting female connector 3/4 " O.D. , FEMALE CONNECTOR | 0.65
instrument tube fitting female connector 1 " O.D. , FEMALE CONNECTOR | 0.75
instrument tube fitting female connector 1- 1/4 " O.D. , FEMALE CONNECTOR | 0.95
instrument tube fitting female connector 1- 1/2 " O.D. , FEMALE CONNECTOR | 1.1
instrument tube fitting female connector 2 " O.D. , FEMALE CONNECTOR | 1.2
instrument tube fitting union adaptor 3/8 " O.D. , UNION ADAPTOR | 0.25
instrument tube fitting union adaptor 1/2 " O.D. , UNION ADAPTOR | 0.35
instrument tube fitting union adaptor 5/8 " O.D. , UNION ADAPTOR | 0.45
instrument tube fitting union adaptor 3/4 " O.D. , UNION ADAPTOR | 0.55
instrument tube fitting union adaptor 1 " O.D. , UNION ADAPTOR | 0.7
instrument tube fitting union adaptor 1- 1/4 " O.D. , UNION ADAPTOR | 0.9
instrument tube fitting union adaptor 1- 1/2 " O.D. , UNION ADAPTOR | 1.1
instrument tube fitting union adaptor 2 " O.D. , UNION ADAPTOR | 1.2
instrument tube fitting hydrotest 3/8 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 1/2 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 5/8 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 3/4 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 1 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 1- 1/4 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 1- 1/2 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hydrotest 2 " O.D. , HYDRO TEST | 0.502
instrument tube fitting hangers 3/8 " O.D. , HANGERS | 0.7
instrument tube fitting hangers 1/2 " O.D. , HANGERS | 0.7
instrument tube fitting hangers 5/8 " O.D. , HANGERS | 0.7
instrument tube fitting hangers 3/4 " O.D. , HANGERS | 0.8
instrument tube fitting hangers 1 " O.D. , HANGERS | 0.9
instrument tube fitting hangers 1- 1/4 " O.D. , HANGERS | 0.9
instrument tube fitting hangers 1- 1/2 " O.D. , HANGERS | 1
instrument tube fitting hangers 2 " O.D. , HANGERS | 1.25
instrument pipe stanchion (stand) pipe stanchion FABRICATE & INSTALL PIPE STANCHION Assembly | 7.82
instrument tube fitting-air supply 1/2 " PIPE 1/2 " PIPE | 0.69
instrument tube fitting-air supply 1/2 " 90 DEG. ELL SCRD 1/2 " 90 DEG. ELL SCRD | 0.48
instrument tube fitting-air supply 1/2 " TEE SCRD 1/2 " TEE SCRD | 0.68
instrument tube fitting-air supply 1/2 " X 6 " NIPPLE 1/2 " X 6 " NIPPLE | 0.48
instrument tube fitting-air supply 1/2 " PLUG 1/2 " PLUG | 0.48
instrument tube fitting-air supply 1/2 " BALL VALVE 1/2 " BALL VALVE | 0.51
instrument tube fitting-air supply PIPE SUPPORT PIPE SUPPORT | 0.9
instrument tube fitting-air supply - - | -
instrument instrument stand 2 " PIPE 2 " PIPE | 1.2
instrument instrument stand 2 " PIPE CAP 2 " PIPE CAP | 1.2
instrument instrument stand PLATE 9 " X 9 " X 1/2 " PLATE 9 " X 9 " X 1/2 " | 1.2
instrument instrument stand HOOK ANCHOR 1/2 " X 6 " HOOK ANCHOR 1/2 " X 6 " | 2
instrument instrument stand NUT 1/2 " NUT 1/2 " | 0.5
instrument instrument stand - - | -
equipment instrument equipment DCS Control Desk DCS Control Desk | 40
equipment instrument equipment DCS Aux. Desk DCS Aux. Desk | 40
equipment instrument equipment DCS Peripherals such as printers, copiers DCS Peripherals such as printers, copiers | 30
equipment instrument equipment Cabinet Cabinet | 30
equipment instrument equipment Marshalling Cabinets Marshalling Cabinets | 30
equipment instrument equipment Power Distribution Boards Power Distribution Boards | 40
equipment instrument equipment Interface Cabinet Interface Cabinet | 50
equipment instrument equipment ITV Monitor ITV Monitor | 20
equipment instrument equipment UPS UPS | 40
equipment instrument equipment Battery Battery | 40
equipment instrument equipment Instrument Terminal Box Instrument Terminal Box | 30
equipment instrument equipment - - | -
instrument calibration alarm - INSTRUMENT TYPE - ALARMS | Cal/Test
instrument calibration alarm - ANALYZER ALARM - HIGH AND LOW | 1
instrument calibration alarm - BURNER ALARM - HIGH AND LOW | 1
instrument calibration alarm - FLOW ALARM | 1
instrument calibration alarm - FLOW ALARM - HIGH | 1
instrument calibration alarm - FLOW ALARM - HIGH / LOW | 1
instrument calibration alarm - FLOW ALARM - LOW | 1
instrument calibration alarm - FLOW ALARM - LOW / HIGH | 0
instrument calibration alarm - FLOW ALARM - LOW / LOW | 0
instrument calibration alarm - LEVEL ALARM | 1
instrument calibration alarm - LEVEL ALARM - HIGH | 1
instrument calibration alarm - LEVEL ALARM - HIGH HIGH | 0
instrument calibration alarm - LEVEL ALARM - HIGH / LOW | 1
instrument calibration alarm - LEVEL ALARM - LOW | 1
instrument calibration alarm - LEVEL ALARM - LOW / HIGH | 0
instrument calibration alarm - LEVEL ALARM - LOW LOW | 0
instrument calibration alarm - PRESURRE ALARM - | 1
instrument calibration alarm - PRESURRE ALARM - HIGH | 1
instrument calibration alarm - PRESURRE ALARM - HIGH HIGH | 0
instrument calibration alarm - PRESURRE ALARM - HIGH / LOW | 1
instrument calibration alarm - PRESURRE ALARM - LOW | 1
instrument calibration alarm - PRESURRE ALARM - LOW / HIGH | 0
instrument calibration alarm - PRESURRE ALARM - LOW LOW | 0
instrument calibration alarm - PRESURRE DIFF. ALARM HIGH | 0
instrument calibration alarm - PRESURRE DIFF. ALARM HIGH HIGH | 0
instrument calibration alarm - TEMPERATURE ALARM | 1
instrument calibration alarm - TEMPERATURE ALARM - HIGH | 1
instrument calibration alarm - TEMPERATURE ALARM - HIGH HIGH | 0
instrument calibration alarm - TEMPERATURE ALARM - HIGH / LOW | 1
instrument calibration alarm - TEMPERATURE ALARM - LOW | 1
instrument calibration alarm - TEMPERATURE ALARM - LOW / HIGH | 0
instrument calibration alarm - ALARM | 1
instrument calibration control valves - INSTRUMENT TYPE - CONTROL VALVES | Cal/Test
instrument calibration control valves - ANALYZER VALVE | 4
instrument calibration control valves - CONTROL VALVE | 3
instrument calibration control valves - FLOW CONTROL VALVE | 4
instrument calibration control valves - FLOW VALVE | 4
instrument calibration control valves - HAND CONTROL VALVE | 4
instrument calibration control valves - HAND VALVE | 4
instrument calibration control valves - LEVEL CONTROL VALVE | 4
instrument calibration control valves - LEVEL VALVE | 4
instrument calibration control valves - PRESSURE CONTROL VALVE | 4
instrument calibration control valves - PRESSURE VALVE | 4
instrument calibration control valves - TEMPERATURE CONTROL VALVE | 4
instrument calibration control valves - TEMPERATURE VALVE | 4
instrument calibration control valves - CONTROL VALVE | 4
instrument calibration control valves - - | -
instrument calibration controllers - INSTRUMENT TYPE - CONTROLLERS | Cal/Test
instrument calibration controllers - ANALYZER CONTROLLER | 5
instrument calibration controllers - FLOW CONTROLLER | 4
instrument calibration controllers - HAND CONTROLLER ( MANUAL ) | 1
instrument calibration controllers - HAND INDICATING CONTROLLER (MANUAL) | 1
instrument calibration controllers - TIME CONTROLLER ( MANUAL ) | 3
instrument calibration controllers - LEVEL CONTROLLER | 3
instrument calibration controllers - PRESSURE CONTROLLER | 5
instrument calibration controllers - TEMPERATURE CONTROLLER | 6
instrument calibration controllers - WEIGHT CONTROLLER | 4
instrument calibration elements - INSTRUMENT TYPE - ELEMENTS | Cal/Test
instrument calibration elements - ANALYZER ELEMENT | 0
instrument calibration elements - BURNER ELEMENT | 0.5
instrument calibration elements - CONDUCTIVITY ELEMENT | 0.5
instrument calibration elements - DENSITY ELEMENT | 0.5
instrument calibration elements - FLOW ELEMENT ( ORIFICE PLATE ) | 0.5
instrument calibration elements - ORIFICE PLATE | 0.5
instrument calibration elements - CURRENT ELEMENT | 2
instrument calibration elements - LEVEL ELEMENT | 0.5
instrument calibration elements - MOISTURE ELEMENT | 22
instrument calibration elements - PRESSURE ELEMENT | 4
instrument calibration elements - RESTRICTION ORIFICE | 0.5
instrument calibration elements - SPEED ELEMENT | 0.5
instrument calibration elements - TEMPERATURE ELEMENT | 4
instrument calibration elements - VISCOSITY ELEMENT | 0.5
instrument calibration elements - WEIGHT ELEMENT | 4
instrument calibration elements - - | -
instrument calibration indicators - INSTRUMENT TYPE - INDICATORS | Cal/Test
instrument calibration indicators - ANALYZER INDICATOR | 1
instrument calibration indicators - ANALYZER INDICATING CONTROLLER | 5
instrument calibration indicators - FLOW INDICATOR ( PNEU. TYPE ) | 5
instrument calibration indicators - FLOW INDICATING CONTROLLER | 4
instrument calibration indicators - CURRENT INDICATOR | 1
instrument calibration indicators - ELECTRONIC TIMER | 1
instrument calibration indicators - LEVEL INDICATOR | 4
instrument calibration indicators - LEVEL INDICATING CONTROLLER | 4
instrument calibration indicators - PRESSURE DIFFERENTIAL INDICATOR | 3
instrument calibration indicators - PRESSURE DIFF. INDIC. CONTROLLER | 6
instrument calibration indicators - PRESSURE INDICATOR | 1
instrument calibration indicators - PRESSURE INDICATING CONTROLLER | 5
instrument calibration indicators - TEMPERATURE INDICATOR | 1
instrument calibration indicators - TEMPERATURE INDICATING CONTROLLER | 6
instrument calibration indicators - WEIGHT INDICATOR | 1
instrument calibration indicators - WEIGHT INDICATING CONTROLLER | 4
instrument calibration indicators - POSITION INDICATOR | 0.5
instrument calibration recorders - INSTRUMENT TYPE - RECORDERS | Cal/Test
instrument calibration recorders - ANALYZER RECORDER | 3.5
instrument calibration recorders - FLOW RECORDER | 3.5
instrument calibration recorders - FLOW RECORDER CONTROLLER | 4
instrument calibration recorders - LEVEL RECORDER | 3.5
instrument calibration recorders - PRESSURE RECORDER | 3.5
instrument calibration recorders - PRESSURE RECORDING CONTROLLER | 5
instrument calibration recorders - TEMPERATURE RECORDER | 3.5
instrument calibration recorders - TEMPERATURE RECORDER CONTROLLER | 4
instrument calibration recorders - WEIGHT RECORDER | 4
instrument calibration recorders - - | -
instrument calibration switch - INSTRUMENT TYPE - SWITCHES | Cal/Test
instrument calibration switch - ANALYZER SWITCH HIGH | 0.5
instrument calibration switch - ANALYZER SWITCH LOW | 0.5
instrument calibration switch - BURNER SWITCH | 0.5
instrument calibration switch - BURNER SWITCH HIGH | 0.5
instrument calibration switch - BURNER SWITCH LOW | 0.5
instrument calibration switch - FLOW INDICATING SWITCH | 4
instrument calibration switch - FLOW INDICATING SWITCH HIGH | 4
instrument calibration switch - FLOW INDICATING SWITCH HIGH / LOW | 4
instrument calibration switch - FLOW INDICATING SWITCH LOW | 4
instrument calibration switch - FLOW INDICATING SWITCH LOW / HIGH | 4
instrument calibration switch - FLOW SWITCH | 4
instrument calibration switch - FLOW SWITCH HIGH | 4
instrument calibration switch - FLOW SWITCH HIGH / LOW | 4
instrument calibration switch - FLOW SWITCH LOW | 4
instrument calibration switch - FLOW SWITCH LOW / HIGH | 4
instrument calibration switch - FLOW SWITCH LOW / LOW | 4
instrument calibration switch - HAND SWITCH | 1
instrument calibration switch - CURRENT SWITCH | 1
instrument calibration switch - TIMER SWITCH | 1
instrument calibration switch - LEVEL SWITCH | 6
instrument calibration switch - LEVEL SWITCH HIGH | 6
instrument calibration switch - LEVEL SWITCH HIGH HIGH | 6
instrument calibration switch - LEVEL SWITCH HIGH / LOW | 6
instrument calibration switch - LEVEL SWITCH LOW | 6
instrument calibration switch - LEVEL SWITCH LOW / HIGH | 6
instrument calibration switch - LEVEL SWITCH LOW LOW | 6
instrument calibration switch - PRESSURE DIFF. INDIC. SWITCH | 5
instrument calibration switch - PRESSURE DIFF. INDIC. SWITCH High | 5
instrument calibration switch - PRESSURE DIFF. INDIC. SWITCH High/Low | 5
instrument calibration switch - PRESSURE DIFF. INDIC. SWITCH Low | 5
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH | 2
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH High | 2
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH High/High | 2
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH High/Low | 2
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH Low | 2
instrument calibration switch - PRESSURE DIFFERENTIAL SWITCH Low/High | 2
instrument calibration switch - PRESSURE SWITCH | 2
instrument calibration switch - PRESSURE SAFETY ELEMENT | 0.5
instrument calibration switch - PRESSURE SWITCH HIGH | 2
instrument calibration switch - PRESSURE SWITCH HIGH HIGH | 2
instrument calibration switch - PRESSURE SWITCH HIGH / LOW | 2
instrument calibration switch - PRESSURE SWITCH LOW | 2
instrument calibration switch - PRESSURE SWITCH LOW / HIGH | 2
instrument calibration switch - PRESSURE SWITCH LOW LOW | 2
instrument calibration switch - PRESSURE SAFETY VALVE | 0.5
instrument calibration switch - SPEED SWITCH | 1.5
instrument calibration switch - SPEED SWITCH HIGH | 1.5
instrument calibration switch - SPEED SWITCH LOW | 1.5
instrument calibration switch - TEMPERATURE SWITCH | 1
instrument calibration switch - TEMPERATURE SWITCH HIGH | 1
instrument calibration switch - TEMPERATURE SWITCH LOW | 1
instrument calibration switch - TEMPERATURE SWITCH HIGH LOW | 1
instrument calibration switch - LIMIT SWITCH | 1
instrument calibration switch - LIMIT SWITCH HIGH | 1
instrument calibration switch - LIMIT SWITCH LOW | 1
instrument calibration switch - TEMPERATURE INDICATING SWITCH | 2
instrument calibration switch - TEMPERATURE INDICATING SWITCH High | 5
instrument calibration switch - TEMPERATURE INDICATING SWITCH Low | 5
instrument calibration switch - TEMPERATURE INDICATING SWITCH H/L | 5
instrument calibration switch - LIMIT / PROXIMITY SWITCH | 1
instrument calibration switch - LIMIT / PROXIMITY SWITCH HIGH | 1
instrument calibration switch - LIMIT / PROXIMITY SWITCH LOW | 1
instrument calibration switch - - | -
instrument calibration pressure items - INSTRUMENT TYPE - PRESSURE ITEMS | Cal/Test
instrument calibration pressure items - PRESSURE SAFETY ELEMENT | 1
instrument calibration pressure items - RUPTURE DISK | 1
instrument calibration pressure items - PRESSURE SAFETY VALVE | 1
instrument calibration pressure items - RELIEF VALVE | 1
instrument calibration solenoid valves - INSTRUMENT TYPE - SOLENOID VALVES | Cal/Test
instrument calibration solenoid valves - FLOW SOLENOID | 1
instrument calibration solenoid valves - LEVEL SOLENOID | 1
instrument calibration solenoid valves - PRESSURE SOLENOID | 1
instrument calibration solenoid valves - TEMPERATURE SOLENOID | 1
instrument calibration solenoid valves - SOLENOID VALVE | 0.5
instrument calibration solenoid valves - - | -
instrument calibration transmitter - INSTRUMENT TYPE - TRANSMITTERS | Cal/Test
instrument calibration transmitter - ANALYZER TRANSMITTER | 6
instrument calibration transmitter - ANALYZER INDICATING TRANSMITTER | 6
instrument calibration transmitter - DENSITY TRANSMITTER | 4
instrument calibration transmitter - FLOW TRANSMITTER | 6
instrument calibration transmitter - FLOW INDICATING TRANSMITTER | 6
instrument calibration transmitter - CURRENT TRANSMITTER | 4
instrument calibration transmitter - LEVEL TRANSMITTER | 4
instrument calibration transmitter - LEVEL INDICATING TRANSMITTER | 4
instrument calibration transmitter - MOISTURE TRANSMITTER | 3
instrument calibration transmitter - MOISTURE INDICATING TRANSMITTER | 3
instrument calibration transmitter - PRESSURE TRANSMITTER | 5
instrument calibration transmitter - PRESSURE INDICATING TRANSMITTER | 5
instrument calibration transmitter - PRESSURE DIFF. INDICATING TRANSMITTER | 5
instrument calibration transmitter - PRESSURE DIFFERENTIAL TRANSMITTER | 5
instrument calibration transmitter - TEMPERATURE TRANSMITTER | 6
instrument calibration transmitter - TEMPERATURE INDICATING TRANSMITTER | 6
instrument calibration transmitter - TEMPERATURE DIFFERENTIAL TRANSMITTER | 6
instrument calibration transmitter - VISCOSITY TRANSMITTER | 4
instrument calibration transmitter - WEIGHT TRANSMITTER | 4
instrument calibration transmitter - WEIGHT INDICATING TRANSMITTER | 4
instrument calibration I/P Transducer - INSTRUMENT TYPE - I / P TRANSDUCERS | Cal/Test
instrument calibration I/P Transducer - FLOW I / P TRANSDUCER | 2.5
instrument calibration I/P Transducer - LEVEL I / P TRANSDUCER | 2.5
instrument calibration I/P Transducer - PRESSURE I / P TRANSDUCER | 2.5
instrument calibration I/P Transducer - TEMPERATURE I / P TRANSDUCER | 2.5
instrument calibration misc. instruments - INSTRUMENT TYPE - MISC. INSTRUMENTS | Cal/Test
instrument calibration misc. instruments - FLOW TOTALIZER | 3
instrument calibration misc. instruments - FLOW GLASS | 0
instrument calibration misc. instruments - LEVEL GAUGE W/O BRIDLE | 0
instrument calibration misc. instruments - LEVEL GAUGE W/ BRIDLE | 0
instrument calibration misc. instruments - SIGHT GLASS | 0
instrument calibration misc. instruments - - | -
instrument calibration panel mounted instrument - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Cal/Test
instrument calibration panel mounted instrument - LEVEL ALARM HIGH | 0
instrument calibration panel mounted instrument - PRESSURE ALARM LOW | 0
instrument calibration panel mounted instrument - TEMPERATURE ALARM HIGH | 0
instrument calibration panel mounted instrument - TEMPERATURE ALARM LOW | 0
instrument calibration panel mounted instrument - UNCLASSIFIED ALARM | 0
instrument calibration panel mounted instrument - FLOW INDICATOR CONTROLLER | 4
instrument calibration panel mounted instrument - HAND INDICATOR CONTROLLER | 1
instrument calibration panel mounted instrument - PRESSURE INDICATOR CONTROLLER | 3
instrument calibration panel mounted instrument - LEVEL INDICATOR | 2.4
instrument calibration panel mounted instrument - PRESSURE SWITCH LOW | 1
instrument calibration panel mounted instrument - TEMPERATURE SWITCH HIGH | 1
instrument calibration panel mounted instrument - TEMPERATURE SWITCH LOW | 1
instrument calibration panel mounted instrument - UNCLASSIFIED SPEED SWITCH | 1
instrument calibration panel mounted instrument - AIR SWITCH | 0
instrument calibration panel mounted instrument - ANNUNCIATOR POINT, PILOT LIGHT, ALARM | 0
instrument calibration panel mounted instrument - AUTO / MANUAL SWITCHING STATION | 0
instrument calibration panel mounted instrument - - | -
instrument calibration panel mounted instrument - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Cal/Test
instrument calibration panel mounted instrument - ONE POINT | 2
instrument calibration panel mounted instrument - TWO POINT | 3
instrument calibration panel mounted instrument - ONE PEN | 3
instrument calibration panel mounted instrument - TWO PEN | 4.5
instrument calibration panel mounted instrument - THREE PEN | 6.5
instrument calibration panel mounted instrument - ONE PEN | 5
instrument calibration panel mounted instrument - TWO PEN | 7
instrument calibration panel mounted instrument - THREE PEN | 9
instrument calibration panel mounted instrument - MULTIPOINT TEMPERATURE INDICATOR | 3
instrument calibration panel mounted instrument - PER POINT TI | 0.5
instrument calibration panel mounted instrument - MULTIPOINT TEMPERATURE RECORDER | 4
instrument calibration panel mounted instrument - PER POINT TR | 0.5
instrument calibration panel mounted instrument - DRAFT GAUGE ONE POINT | 5
instrument calibration panel mounted instrument - ADD FOR EACH POINT PI | 1
instrument calibration panel mounted instrument - ANNUNCIATOR SYSTEM | 4.8
instrument calibration panel mounted instrument - ADD FOR EACH POINT | 0.5
instrument calibration panel mounted instrument - INTEGRATOR | 3.5
instrument calibration panel mounted instrument - VOLTAGE OR AMMETER | 2
instrument calibration panel mounted instrument - PUSHBUTTONS | 1
instrument calibration panel mounted instrument - LIGHTS | 1
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( ELECT ) | 1
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( PNEU ) 3 - WAY | 2
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( PNEU ) 4 - WAY | 2.5
instrument calibration panel mounted instrument - FUNCTION GENERATOR | 5
instrument calibration panel mounted instrument - TRANSDUCERS | 4.5
instrument calibration panel mounted instrument - CIRCUIT BREAKERS | 4.5
instrument calibration panel mounted instrument - TERMINAL BOX | 1
instrument calibration panel mounted instrument - DISTRIBUTION PANEL | 1
instrument calibration panel mounted instrument - ( CONT'N. ) | Cal/Test
instrument calibration panel mounted instrument - RELAYS | 2
instrument calibration panel mounted instrument - LIMIT HIGH | 1.5
instrument calibration panel mounted instrument - LIMIT LOW | 1.5
instrument calibration panel mounted instrument - SELECTOR, HIGH OR LOW | 1.5
instrument calibration panel mounted instrument - BOOSTER | 1.5
instrument calibration panel mounted instrument - REVERSING | 1.5
instrument calibration panel mounted instrument - SWITCHES ( RECEIVER TYPE ) SINGLE | 2
instrument calibration panel mounted instrument - SWITCHES ( RECEIVER TYPE ) DUAL | 4
instrument calibration panel mounted instrument - POWER SUPPLY | 2
instrument calibration panel mounted instrument - CLOCK | 1
instrument calibration panel mounted instrument - AMPLIFIER | 4
instrument calibration panel mounted instrument - ALARM HORN | 1
instrument calibration panel mounted instrument - ALARM MODULE PER POINT | 1
instrument calibration panel mounted instrument - SOLENOID - 2 WAY | 2
instrument calibration panel mounted instrument - SOLENOID - 3 WAY | 2
instrument calibration panel mounted instrument - SOLENOID - 4 WAY | 2
instrument calibration loop checking - INSTRUMENT TYPE - ALARMS | Loop Ck.
instrument calibration loop checking - ANALYZER ALARM - HIGH AND LOW | 1.5
instrument calibration loop checking - BURNER ALARM - HIGH AND LOW | 1.5
instrument calibration loop checking - FLOW ALARM | 1.5
instrument calibration loop checking - FLOW ALARM - HIGH | 1.5
instrument calibration loop checking - FLOW ALARM - HIGH / LOW | 1.5
instrument calibration loop checking - FLOW ALARM - LOW | 1.5
instrument calibration loop checking - FLOW ALARM - LOW / HIGH | 1.5
instrument calibration loop checking - FLOW ALARM - LOW / LOW | 1.5
instrument calibration loop checking - LEVEL ALARM | 1.5
instrument calibration loop checking - LEVEL ALARM - HIGH | 1.5
instrument calibration loop checking - LEVEL ALARM - HIGH HIGH | 1.5
instrument calibration loop checking - LEVEL ALARM - HIGH / LOW | 1.5
instrument calibration loop checking - LEVEL ALARM - LOW | 1.5
instrument calibration loop checking - LEVEL ALARM - LOW / HIGH | 1.5
instrument calibration loop checking - LEVEL ALARM - LOW LOW | 1.5
instrument calibration loop checking - PRESURRE ALARM - | 1.5
instrument calibration loop checking - PRESURRE ALARM - HIGH | 1.5
instrument calibration loop checking - PRESURRE ALARM - HIGH HIGH | 1.5
instrument calibration loop checking - PRESURRE ALARM - HIGH / LOW | 1.5
instrument calibration loop checking - PRESURRE ALARM - LOW | 1.5
instrument calibration loop checking - PRESURRE ALARM - LOW / HIGH | 1.5
instrument calibration loop checking - PRESURRE ALARM - LOW LOW | 1.5
instrument calibration loop checking - PRESURRE DIFF. ALARM HIGH | 1.5
instrument calibration loop checking - PRESURRE DIFF. ALARM HIGH HIGH | 1.5
instrument calibration loop checking - TEMPERATURE ALARM | 1.5
instrument calibration loop checking - TEMPERATURE ALARM - HIGH | 1.5
instrument calibration loop checking - TEMPERATURE ALARM - HIGH HIGH | 1.5
instrument calibration loop checking - TEMPERATURE ALARM - HIGH / LOW | 1.5
instrument calibration loop checking - TEMPERATURE ALARM - LOW | 1.5
instrument calibration loop checking - TEMPERATURE ALARM - LOW / HIGH | 1.5
instrument calibration loop checking - ALARM | 1.5
instrument calibration control valves - INSTRUMENT TYPE - CONTROL VALVES | Loop Ck.
instrument calibration control valves - ANALYZER VALVE | 1.5
instrument calibration control valves - CONTROL VALVE | 1.5
instrument calibration control valves - FLOW CONTROL VALVE | 1.5
instrument calibration control valves - FLOW VALVE | 1.5
instrument calibration control valves - HAND CONTROL VALVE | 1.5
instrument calibration control valves - HAND VALVE | 1.5
instrument calibration control valves - LEVEL CONTROL VALVE | 1.5
instrument calibration control valves - LEVEL VALVE | 1.5
instrument calibration control valves - PRESSURE CONTROL VALVE | 1.5
instrument calibration control valves - PRESSURE VALVE | 1.5
instrument calibration control valves - TEMPERATURE CONTROL VALVE | 1.5
instrument calibration control valves - TEMPERATURE VALVE | 1.5
instrument calibration control valves - CONTROL VALVE | 1.5
instrument calibration controllers - INSTRUMENT TYPE - CONTROLLERS | Loop Ck.
instrument calibration controllers - ANALYZER CONTROLLER | 1.5
instrument calibration controllers - FLOW CONTROLLER | 1.5
instrument calibration controllers - HAND CONTROLLER ( MANUAL ) | 1.5
instrument calibration controllers - HAND INDICATING CONTROLLER (MANUAL) | 1.5
instrument calibration controllers - TIME CONTROLLER ( MANUAL ) | 1.5
instrument calibration controllers - LEVEL CONTROLLER | 1.5
instrument calibration controllers - PRESSURE CONTROLLER | 1.5
instrument calibration controllers - TEMPERATURE CONTROLLER | 1.5
instrument calibration controllers - WEIGHT CONTROLLER | 1.5
instrument calibration controllers - INSTRUMENT TYPE - ELEMENTS | Loop Ck.
instrument calibration controllers - ANALYZER ELEMENT | 1.5
instrument calibration controllers - BURNER ELEMENT | 1.5
instrument calibration controllers - CONDUCTIVITY ELEMENT | 1.5
instrument calibration controllers - DENSITY ELEMENT | 1.5
instrument calibration controllers - FLOW ELEMENT ( ORIFICE PLATE ) | 1.5
instrument calibration controllers - ORIFICE PLATE | 1.5
instrument calibration controllers - CURRENT ELEMENT | 1.5
instrument calibration controllers - LEVEL ELEMENT | 1.5
instrument calibration controllers - MOISTURE ELEMENT | 1.5
instrument calibration controllers - PRESSURE ELEMENT | 1.5
instrument calibration controllers - RESTRICTION ORIFICE | 1.5
instrument calibration controllers - SPEED ELEMENT | 1.5
instrument calibration controllers - TEMPERATURE ELEMENT | 1.5
instrument calibration controllers - VISCOSITY ELEMENT | 1.5
instrument calibration controllers - WEIGHT ELEMENT | 1.5
instrument calibration indicator - INSTRUMENT TYPE - INDICATORS | Loop Ck.
instrument calibration indicator - ANALYZER INDICATOR | 1.5
instrument calibration indicator - ANALYZER INDICATING CONTROLLER | 1.5
instrument calibration indicator - FLOW INDICATOR ( PNEU. TYPE ) | 1.5
instrument calibration indicator - FLOW INDICATING CONTROLLER | 1.5
instrument calibration indicator - CURRENT INDICATOR | 1.5
instrument calibration indicator - ELECTRONIC TIMER | 1.5
instrument calibration indicator - LEVEL INDICATOR | 1.5
instrument calibration indicator - LEVEL INDICATING CONTROLLER | 1.5
instrument calibration indicator - PRESSURE DIFFERENTIAL INDICATOR | 1.5
instrument calibration indicator - PRESSURE DIFF. INDIC. CONTROLLER | 1.5
instrument calibration indicator - PRESSURE INDICATOR | 1.5
instrument calibration indicator - PRESSURE INDICATING CONTROLLER | 1.5
instrument calibration indicator - TEMPERATURE INDICATOR | 1.5
instrument calibration indicator - TEMPERATURE INDICATING CONTROLLER | 1.5
instrument calibration indicator - WEIGHT INDICATOR | 1.5
instrument calibration indicator - WEIGHT INDICATING CONTROLLER | 1.5
instrument calibration indicator - POSITION INDICATOR | 1.5
instrument calibration recorder - INSTRUMENT TYPE - RECORDERS | Loop Ck.
instrument calibration recorder - ANALYZER RECORDER | 1.5
instrument calibration recorder - FLOW RECORDER | 1.5
instrument calibration recorder - FLOW RECORDER CONTROLLER | 1.5
instrument calibration recorder - LEVEL RECORDER | 1.5
instrument calibration recorder - PRESSURE RECORDER | 1.5
instrument calibration recorder - PRESSURE RECORDING CONTROLLER | 1.5
instrument calibration recorder - TEMPERATURE RECORDER | 1.5
instrument calibration recorder - TEMPERATURE RECORDER CONTROLLER | 1.5
instrument calibration recorder - WEIGHT RECORDER | 1.5
instrument calibration switches - INSTRUMENT TYPE - SWITCHES | Loop Ck.
instrument calibration switches - ANALYZER SWITCH HIGH | 1.5
instrument calibration switches - ANALYZER SWITCH LOW | 1.5
instrument calibration switches - BURNER SWITCH | 1.5
instrument calibration switches - BURNER SWITCH HIGH | 1.5
instrument calibration switches - BURNER SWITCH LOW | 1.5
instrument calibration switches - FLOW INDICATING SWITCH | 1.5
instrument calibration switches - FLOW INDICATING SWITCH HIGH | 1.5
instrument calibration switches - FLOW INDICATING SWITCH HIGH / LOW | 1.5
instrument calibration switches - FLOW INDICATING SWITCH LOW | 1.5
instrument calibration switches - FLOW INDICATING SWITCH LOW / HIGH | 1.5
instrument calibration switches - FLOW SWITCH | 1.5
instrument calibration switches - FLOW SWITCH HIGH | 1.5
instrument calibration switches - FLOW SWITCH HIGH / LOW | 1.5
instrument calibration switches - FLOW SWITCH LOW | 1.5
instrument calibration switches - FLOW SWITCH LOW / HIGH | 1.5
instrument calibration switches - FLOW SWITCH LOW / LOW | 1.5
instrument calibration switches - HAND SWITCH | 1.5
instrument calibration switches - CURRENT SWITCH | 1.5
instrument calibration switches - TIMER SWITCH | 1.5
instrument calibration switches - LEVEL SWITCH | 1.5
instrument calibration switches - LEVEL SWITCH HIGH | 1.5
instrument calibration switches - LEVEL SWITCH HIGH HIGH | 1.5
instrument calibration switches - LEVEL SWITCH HIGH / LOW | 1.5
instrument calibration switches - LEVEL SWITCH LOW | 1.5
instrument calibration switches - LEVEL SWITCH LOW / HIGH | 1.5
instrument calibration switches - LEVEL SWITCH LOW LOW | 1.5
instrument calibration switches - PRESSURE DIFF. INDIC. SWITCH | 1.5
instrument calibration switches - PRESSURE DIFF. INDIC. SWITCH High | 1.5
instrument calibration switches - PRESSURE DIFF. INDIC. SWITCH High/Low | 1.5
instrument calibration switches - PRESSURE DIFF. INDIC. SWITCH Low | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH High | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH High/High | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH High/Low | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH Low | 1.5
instrument calibration switches - PRESSURE DIFFERENTIAL SWITCH Low/High | 1.5
instrument calibration switches - PRESSURE SWITCH | 1.5
instrument calibration switches - PRESSURE SAFETY ELEMENT | 0
instrument calibration switches - PRESSURE SWITCH HIGH | 1.5
instrument calibration switches - PRESSURE SWITCH HIGH HIGH | 1.5
instrument calibration switches - PRESSURE SWITCH HIGH / LOW | 1.5
instrument calibration switches - PRESSURE SWITCH LOW | 1.5
instrument calibration switches - PRESSURE SWITCH LOW / HIGH | 1.5
instrument calibration switches - PRESSURE SWITCH LOW LOW | 1.5
instrument calibration switches - PRESSURE SAFETY VALVE | 1.5
instrument calibration switches - SPEED SWITCH | 1.5
instrument calibration switches - SPEED SWITCH HIGH | 1.5
instrument calibration switches - SPEED SWITCH LOW | 1.5
instrument calibration switches - TEMPERATURE SWITCH | 1.5
instrument calibration switches - TEMPERATURE SWITCH HIGH | 1.5
instrument calibration switches - TEMPERATURE SWITCH LOW | 1.5
instrument calibration switches - TEMPERATURE SWITCH HIGH LOW | 1.5
instrument calibration switches - LIMIT SWITCH | 1.5
instrument calibration switches - LIMIT SWITCH HIGH | 1.5
instrument calibration switches - LIMIT SWITCH LOW | 1.5
instrument calibration switches - TEMPERATURE INDICATING SWITCH | 1.5
instrument calibration switches - TEMPERATURE INDICATING SWITCH High | 1.5
instrument calibration switches - TEMPERATURE INDICATING SWITCH Low | 1.5
instrument calibration switches - TEMPERATURE INDICATING SWITCH H/L | 1.5
instrument calibration switches - LIMIT / PROXIMITY SWITCH | 1.5
instrument calibration switches - LIMIT / PROXIMITY SWITCH HIGH | 1.5
instrument calibration switches - LIMIT / PROXIMITY SWITCH LOW | 1.5
instrument calibration pressure - INSTRUMENT TYPE - PRESSURE ITEMS | Loop Ck.
instrument calibration pressure - PRESSURE SAFETY ELEMENT | 0
instrument calibration pressure - RUPTURE DISK | 0
instrument calibration pressure - PRESSURE SAFETY VALVE | 0
instrument calibration pressure - RELIEF VALVE | 0
instrument calibration solenoid valves - INSTRUMENT TYPE - SOLENOID VALVES | Loop Ck.
instrument calibration solenoid valves - FLOW SOLENOID | 1.5
instrument calibration solenoid valves - LEVEL SOLENOID | 1.5
instrument calibration solenoid valves - PRESSURE SOLENOID | 1.5
instrument calibration solenoid valves - TEMPERATURE SOLENOID | 1.5
instrument calibration solenoid valves - SOLENOID VALVE | 1.5
instrument calibration transmitters - INSTRUMENT TYPE - TRANSMITTERS | Loop Ck.
instrument calibration transmitters - ANALYZER TRANSMITTER | 1.5
instrument calibration transmitters - ANALYZER INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - DENSITY TRANSMITTER | 1.5
instrument calibration transmitters - FLOW TRANSMITTER | 1.5
instrument calibration transmitters - FLOW INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - CURRENT TRANSMITTER | 1.5
instrument calibration transmitters - LEVEL TRANSMITTER | 1.5
instrument calibration transmitters - LEVEL INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - MOISTURE TRANSMITTER | 1.5
instrument calibration transmitters - MOISTURE INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - PRESSURE TRANSMITTER | 1.5
instrument calibration transmitters - PRESSURE INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - PRESSURE DIFF. INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - PRESSURE DIFFERENTIAL TRANSMITTER | 1.5
instrument calibration transmitters - TEMPERATURE TRANSMITTER | 1.5
instrument calibration transmitters - TEMPERATURE INDICATING TRANSMITTER | 1.5
instrument calibration transmitters - TEMPERATURE DIFFERENTIAL TRANSMITTER | 1.5
instrument calibration transmitters - VISCOSITY TRANSMITTER | 1.5
instrument calibration transmitters - WEIGHT TRANSMITTER | 1.5
instrument calibration transmitters - WEIGHT INDICATING TRANSMITTER | 1.5
instrument calibration I/P transducer - INSTRUMENT TYPE - I / P TRANSDUCERS | Loop Ck.
instrument calibration I/P transducer - FLOW I / P TRANSDUCER | 1.5
instrument calibration I/P transducer - LEVEL I / P TRANSDUCER | 1.5
instrument calibration I/P transducer - PRESSURE I / P TRANSDUCER | 1.5
instrument calibration I/P transducer - TEMPERATURE I / P TRANSDUCER | 1.5
instrument calibration misc. instrument - INSTRUMENT TYPE - MISC. INSTRUMENTS | Loop Ck.
instrument calibration misc. instrument - FLOW TOTALIZER | 1.5
instrument calibration misc. instrument - FLOW GLASS | 0
instrument calibration misc. instrument - LEVEL GAUGE W/O BRIDLE | 1.5
instrument calibration misc. instrument - LEVEL GAUGE W/ BRIDLE | 0
instrument calibration misc. instrument - SIGHT GLASS | 0
instrument calibration panel mounted instrument - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Loop Ck.
instrument calibration panel mounted instrument - LEVEL ALARM HIGH | 1.5
instrument calibration panel mounted instrument - PRESSURE ALARM LOW | 1.5
instrument calibration panel mounted instrument - TEMPERATURE ALARM HIGH | 1.5
instrument calibration panel mounted instrument - TEMPERATURE ALARM LOW | 1.5
instrument calibration panel mounted instrument - UNCLASSIFIED ALARM | 1.5
instrument calibration panel mounted instrument - FLOW INDICATOR CONTROLLER | 1.5
instrument calibration panel mounted instrument - HAND INDICATOR CONTROLLER | 1.5
instrument calibration panel mounted instrument - PRESSURE INDICATOR CONTROLLER | 1.5
instrument calibration panel mounted instrument - LEVEL INDICATOR | 1.5
instrument calibration panel mounted instrument - PRESSURE SWITCH LOW | 1.5
instrument calibration panel mounted instrument - TEMPERATURE SWITCH HIGH | 1.5
instrument calibration panel mounted instrument - TEMPERATURE SWITCH LOW | 1.5
instrument calibration panel mounted instrument - UNCLASSIFIED SPEED SWITCH | 1.5
instrument calibration panel mounted instrument - AIR SWITCH | 0
instrument calibration panel mounted instrument - ANNUNCIATOR POINT, PILOT LIGHT, ALARM | 0
instrument calibration panel mounted instrument - AUTO / MANUAL SWITCHING STATION | 0
instrument calibration panel mounted instrument - INSTRUMENT TYPE - PANEL MTD. INSTRUMENTS | Loop Ck.
instrument calibration panel mounted instrument - ONE POINT | 1.5
instrument calibration panel mounted instrument - TWO POINT | 1.5
instrument calibration panel mounted instrument - ONE PEN | 1.5
instrument calibration panel mounted instrument - TWO PEN | 1.5
instrument calibration panel mounted instrument - THREE PEN | 1.5
instrument calibration panel mounted instrument - ONE PEN | 1.5
instrument calibration panel mounted instrument - TWO PEN | 1.5
instrument calibration panel mounted instrument - THREE PEN | 1.5
instrument calibration panel mounted instrument - MULTIPOINT TEMPERATURE INDICATOR | 1.5
instrument calibration panel mounted instrument - PER POINT TI | 0
instrument calibration panel mounted instrument - MULTIPOINT TEMPERATURE RECORDER | 1.5
instrument calibration panel mounted instrument - PER POINT TR | 0
instrument calibration panel mounted instrument - DRAFT GAUGE ONE POINT | 1.5
instrument calibration panel mounted instrument - ADD FOR EACH POINT PI | 0
instrument calibration panel mounted instrument - ANNUNCIATOR SYSTEM | 1.5
instrument calibration panel mounted instrument - ADD FOR EACH POINT | 0
instrument calibration panel mounted instrument - INTEGRATOR | 1.5
instrument calibration panel mounted instrument - VOLTAGE OR AMMETER | 1.5
instrument calibration panel mounted instrument - PUSHBUTTONS | 1.5
instrument calibration panel mounted instrument - LIGHTS | 1.5
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( ELECT ) | 1.5
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( PNEU ) 3 - WAY | 1.5
instrument calibration panel mounted instrument - SELECTOR SWITCHES ( PNEU ) 4 - WAY | 1.5
instrument calibration panel mounted instrument - FUNCTION GENERATOR | 1.5
instrument calibration panel mounted instrument - TRANSDUCERS | 0
instrument calibration panel mounted instrument - CIRCUIT BREAKERS | 0
instrument calibration panel mounted instrument - TERMINAL BOX | 0
instrument calibration panel mounted instrument - DISTRIBUTION PANEL | 0
Limit High | 2
Limit Low | 1.5
Selector, High or Low | 1.5
Booster | 1.5
Reversing | 1.5
Switches (Receiver Type) Single | 2
Switches (Receiver Type) Dual | 4
Power Supply | 2
Clock | 1
Amplifier | 4
Alarm Horn | 1
Alarm Module per point | 1
Solenoid - 2 Way | 2
Solenoid - 3 Way | 2
Solenoid - 4 Way | 2
auxiliary system telephone Central Switchboards - Set and Mount in Place Central Switchboards - Set and Mount in Place | 10
auxiliary system telephone - Connections per Pair of Term. - Connections per Pair of Term. | 0.3
auxiliary system telephone Local Stations - Flush Mounted Talk Back Speaker Local Stations - Flush Mounted Talk Back Speaker | 3
auxiliary system telephone - Surface Mounted Talk Back Speaker - Surface Mounted Talk Back Speaker | 2.5
auxiliary system telephone - Suspended Wall Handset - Suspended Wall Handset | 2
auxiliary system telephone - Suspended Desk Handset - Suspended Desk Handset | 2
auxiliary system telephone - Cradle Desk Set - Cradle Desk Set | 1.5
auxiliary system telephone Master Station - Per Terminal Master Station - Per Terminal | 0.6
auxiliary system telephone Substations Substations | 2
fire alarm system fire alarm system 10 Zones 10 Zones | 10
fire alarm system fire alarm system 20 Zones 20 Zones | 14
fire alarm system fire alarm system 30 Zones 30 Zones | 16
fire alarm system fire alarm system 40 Zones 40 Zones | 20
fire alarm system fire alarm system 50 Zones 50 Zones | 24
fire alarm system fire alarm system 100 Zones 100 Zones | 30
fire alarm system fire alarm system Fire Alarm Bell Fire Alarm Bell | 4
fire alarm system fire alarm system Heat Detector Heat Detector | 3
fire alarm system fire alarm system Smoke Detector Smoke Detector | 3
fire alarm system fire alarm system Manual Pull Station Manual Pull Station | 4
fire alarm system fire alarm system Annunciator Annunciator | 10
paging system public address system - Amplifiers - Mounting | 6
paging system public address system - Amplifiers - Connecting Per Terminal | 0.3
paging system public address system - Microphone - Outlet | 1
paging system public address system - Microphone - Mounting and Connecting | 1
paging system public address system - Speakers - Flush Wall - Mtng. and Connecting | 2
paging system public address system - Speakers - Flush Ceilingl - Mtng. and Connecting | 2.5
paging system public address system - Speakers - Surface Wall - Mtng. and Connecting | 1.5
paging system public address system - Trumpet Spkrs - Indoor Wall - Mtng.& Connecting | 3
paging system public address system - Trumpet Spkrs - Outdoor Wall - Mtng. & Connecting | 4
paging system public address system - Trumpet Spkrs - Outdoor Pole - Mtng. & Connecting | 5
paging system paging system - Visual Selector 3 - Digit Keyboard | 10
paging system paging system - Visual Control Relay Panel | 6
paging system paging system - Visual Annunciators - Flush Mounted | 3
paging system paging system - Visual Annunciators - Surface Mounted | 2
paging system paging system - Voice Selector Keyboard | 8
paging system paging system - Voice Microphone | 1
paging system paging system - Voice Amplifier and Power Unit | 4.5
paging system paging system - Voice Terminal Connector Panel | 6
paging system paging system - Voice Loud Speakers - Flush Mounted | 2.5
paging system paging system - Voice Loud Speakers - Surface Mounted | 1.5
audio/video system audio/video system Handset Handset | 0.75
audio/video system audio/video system Monitor Monitor | 3
audio/video system audio/video system Wiring Adapter Wiring Adapter | 1
audio/video system audio/video system Door Station Door Station | 4
audio/video system audio/video system Entrance station Entrance station | 10
audio/video system audio/video system Security Unit Security Unit | 15
audio/video system audio/video system Power Supply Power Supply | 6
audio/video system audio/video system Video Wiring Adaptor Video Wiring Adaptor | 1
cctv system cctv system Camera Camera | 3
cctv system cctv system Pan/Tilt Unit Pan/Tilt Unit | 3
cctv system cctv system Pan/Tilt Controller Pan/Tilt Controller | 3
cctv system cctv system Motorized Zoom Lens Motorized Zoom Lens | 3
cctv system cctv system Multiplexer Multiplexer | 7.5
cctv system cctv system Time Lapse VCR Time Lapse VCR | 5
cctv system cctv system Monitors Monitors | 3
cctv system cctv system Outdoor Antenna Outdoor Antenna | 7.5
cctv system cctv system Indoor Antenna Indoor Antenna | 2
cctv system cctv system Indoor Booster Indoor Booster | 2
cctv system cctv system Amplifier Amplifier | 5
cctv system cctv system Combiner Filter Combiner Filter | 3
cctv system cctv system Splitter Splitter | 2
cctv system cctv system Matching Transformer & UHF/VHF Separator Matching Transformer & UHF/VHF Separator | 0.5
cctv system cctv system Push Plug Push Plug | 0.5
cctv system cctv system TV Socket TV Socket | 0.6
cctv system cctv system Lightning Arrester Lightning Arrester | 4
cctv system cctv system Power Supply Power Supply | 5
cctv system cctv system Frequency Converter Frequency Converter | 4
structured cabling structured cabling Main Distribution Frame ( MDF ) Main Distribution Frame ( MDF ) | 25
structured cabling structured cabling Tenant Distribution Frame ( TDF ) Tenant Distribution Frame ( TDF ) | 20
structured cabling structured cabling Subscriber Distribution Frame ( SDF ) Subscriber Distribution Frame ( SDF ) | 18
structured cabling structured cabling Information Outlets Information Outlets | 1
security access system security access system Security Alarm Control Panel Security Alarm Control Panel | 20
security access system security access system Motion Detector Motion Detector | 3
security access system security access system Magnetic Door Contacts Magnetic Door Contacts | 1.5
security access system security access system Glass Break Detectors Glass Break Detectors | 3
security access system security access system Power Supply for Motion Detectors Power Supply for Motion Detectors | 5
clock system clock system Master Controller - Flush Mounted Master Controller - Flush Mounted | 12
clock system clock system Master Controller - Surface Mounted Master Controller - Surface Mounted | 10
clock system clock system Signal Control Board - Flush Mounted - 20 Signal Signal Control Board - Flush Mounted - 20 Signal | 16
clock system clock system Signal Control Board - Flush Mounted - 30 Signal Signal Control Board - Flush Mounted - 30 Signal | 20
clock system clock system Signal Control Board - Flush Mounted - 40 Signal Signal Control Board - Flush Mounted - 40 Signal | 30
clock system clock system Signal Control Board - Surface Mounted - 20 Signal Signal Control Board - Surface Mounted - 20 Signal | 14
clock system clock system Signal Control Board - Surface Mounted - 30 Signal Signal Control Board - Surface Mounted - 30 Signal | 18
clock system clock system Signal Control Board - Surface Mounted - 40 Signal Signal Control Board - Surface Mounted - 40 Signal | 24
clock system clock system Secondary Clocks - Flush Secondary Clocks - Flush | 2.5
clock system clock system Secondary Clocks - Surface Secondary Clocks - Surface | 2
clock system clock system Secondary Clocks - Double Face Secondary Clocks - Double Face | 2
clock system clock system Bell or Buzzer Contained in Clock Bell or Buzzer Contained in Clock | 1
traffic system traffic system Entry Station w/ ticket issuer, magstripe reader, incl. Entry Station w/ ticket issuer, magstripe reader, incl. | 25
traffic system traffic system Exit station ticket/magstripe reader, including barrier Exit station ticket/magstripe reader, including barrier | 25
traffic system traffic system Loop Detector Loop Detector | 5
traffic system traffic system Payment Station Payment Station | 15
traffic system traffic system Management Computer Management Computer | 20
traffic system traffic system Power Supply with UPS Power Supply with UPS | 10
traffic system traffic system Parking Entrance Indicator System Parking Entrance Indicator System | 7
traffic system traffic system Magnetic Stripe Card and Thermal Paper Magnetic Stripe Card and Thermal Paper | 2.5
traffic system traffic system Thermal Paper Thermal Paper | 0.5
bms bms BMS Control Panel BMS Control Panel | 40
bms bms Direct Digital Controller (DDC) Direct Digital Controller (DDC) | 10
bms bms Automatic Temp. Control Valves (ATC Valve) Automatic Temp. Control Valves (ATC Valve) | 3
bms bms Sensors Sensors | 3
bms bms Indicators Indicators | 3
bms bms Thermometers Thermometers | 3
bms bms Pressure Gauge Pressure Gauge | 3
bms bms Flow Meters Flow Meters | 2
bms bms Flow Switches Flow Switches | 2